## ReadMe
SUMMARY
- This Config_test.xlsx will produce the runner_spec.csv file with the custom selected tests to run for the DMAT and CSR.
- runner_spec.csv is used by run_pscad.py or run_psse.py scripts to run the tests.
TO DO BEFORE RUNNING SCRIPT
1) Ensure correct Suite, Software and WF States are selected in the System_inf tab
2) Ensure correct clauses are selected in the Checklist tab by choosing "Yes" or "No" in the Action column
3) If non suite is selected, for the selected test clause sheets select "Yes" or "No" in the Action column
WORKBOOK INFORMATION
1) Using the "System_inf" tab
- | This sheet is used to specify the parameters for the test sets. The table shows some of the possible inputs.
- | The options in yellow are the common ones to make changes for different run scenarios
| V_POC | Nominal Power | Plant Capacity | Fault level | POC SCR | POC XR ratio | POC base Voltage | Nominal Frequency | Qlead,Qlag | Save Format | Q-V Droop | Suite | Software | WF States | Vgrid | Reference
| 1.034 | 150 | 150 | 901.186 | [12.676303,2.2863071] | [6.66,5.33] | 220 | 50 | [0.3,-0.3] | csv | 0.05 | Run a suite of tests or not | If we want to run tests on PSCAD or PSSE | Describes the wf states which we want to run for. | To select between applying disturbance at either slack bus or using a dummy Tx in PSCAD
[12 empty] | DMAT | PSCAD | ALL | Vslack
[12 empty] | Reduced DMAT | PSSE | WTG PZERO | POC disturbance | Pbase 70, wtg=0
[12 empty] | CSR | Both | BESS PMAX |  | base=150, bess=70
[12 empty] | None |  | BESS PZERO |  | base=150, bess=0
[14 empty] | BESS PMIN |  | base=150, bess=-70
[14 empty] | Pneg, WTG PZERO |  | base=-70, wtg=0
WTG PZERO; BESS PMAX
2) TABLE HEADERS
- | These are already set by default, avoid changing them.
- | Refer to Table 1 for headers of test tables and input options. For the SpecGenerator code to work, it is ESSENTIAL to use the exact header names in Table 1 and input format specified.
- | Every new test sheet created should include the headers under "Must Include" in Table 1
- | Order of headers does not matter
Table 1: (Every sheet must include)
| Info | Test | Action | Software | Suite | End Run (s) | SCR | X/R
| Description: | Test number to be added to the end of the file name. | Manual selection to choose if test will be included in runner_spec | Test for PSSE or PSCAD | Test suite category | Simulation time | Desired Grid SCR Level | Desired Grid X/R
| Options / Exmaples: |  | Yes | PSSE | DMAT | 45 | 12 | 6
|  |  | No | PSCAD | Reduced_DMAT |  | POC | POC
|  |  |  | Both | CSR |  | [12,1]
[5 empty] | None |  | inf | inf
[7 empty] | POC MIN | POC MIN
[7 empty] | POC MAX | POC MAX
WITHSTAND SCR
Table 1a: Optional Headings
| Info | Time Steps (s) | Active Power (pu) | WTG Pref (pu) | BESS Pref (pu) | Pref Deltas (pu) | Pref Ramp (pu/s) | Reactive Power (pu) | Voltage POC (pu) | Voltage POC Deltas (pu) | Voltage POC Ramp (pu/s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Voltage Step (pu) | Vref (pu) | Vref Delta (pu)
| Description: | Time profile for step changes | Wind farm active power reference (applied to BESS or WT depending on WF States from the "System_inf" tab) |  |  | Difference form original P ref at every timestep. |  | Wind farm reactive power setpoint | POC voltage | Difference form original voltage at every timestep. The steps are applied to the Dummy Tx in pscad. | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Difference form original voltage at every timestep. The steps are applied at the slack bus in pscad | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Desired Voltage reference | Difference form original voltage at every timestep. The voltage reference is stepped accordingly
| Options / Exmaples: | [0,5,8] - user defined timesteps | 0.6 |  |  | [0,-0.2,0,0.2,0] - user defined pref_deltas |  | 0.3 | 1.034 | [0,-0.1,0,0.1,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) | 0.1 | 1.034 | Similar to Voltage POC Deltas (pu/s)
|  | fig1 - using a figure from "Figure References" tab for customised profile timesteps | [0, 0.2, 0.4] |  |  | fig1 - using a figure from "Figure References" tab for customised profile pref_deltas |  |  |  | fig1 - using a figure from "Figure References" tab for customised profile voltage deltas | fig1 - using a figure from "Figure References" tab for customised profile voltage ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) |  |  | Similar to Voltage POC Deltas (pu/s)
Table 1b: Optional Headings
| Info | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | Fault X/R | Event | Delta (pu) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | Osc Phase (deg) | Angle Change
| Description: | Time at which a fault is applied | Duration of fault | Fault type | Fault impedance for: - Under voltage faults - Temporary Over Voltage faults (ToV) | Usually matches grid Z, but custom specified for some S5255 tests | Event type if Delta title is used | For a change in value specified in Event, the difference from the original value in pu. | Difference form original freq at every timestep. | Ramp to different freq false/blank - no ramping (infinite step) true - ramp to next value | Grid voltage oscillation frequency | Grid voltage oscillation magntude | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Grid voltage oscillation phase | Grid phase angle change
| Options / Exmaples: | 5 - Single fault applied at time = 5s | 0.25 - Single fault duration | 3PHG | Zf=0 |  | Vref | [0,-0.1,0,0.1,0] - user defined deltas | [0,-1,0,2,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | 0.1 - 0.1Hz oscillation | 0.2 | 0.1 | 2 | 40
|  | [5, 5.5, 6.7] - MFRT | [0.1, 0.1, 0.25] - MFRT | 2PHG | Zf=Zs |  | Vgrid | fig1 - using a figure from "Figure References" tab for customised profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | 0.1:0.9 - Range of oscillations, refer to Table 2 for more info |  |  |  | 40; -40; 60; -60
|  |  | S1 - sequence that defines durations | 1PHG | Zf="K"xZs where K is an integer |  | Qref
|  |  |  | L-L | TOV: Yf = jXc (U_Ov = 1.15pu)
Zf=Rf = 1, 5 and 10 Ohm
S1 -Sequence (MFRT)
3) Test Deliminators
- | The meaning of the general notation of deliminators to differentiate between tests in described
- | Essential to understand when iterating through multiple tests using the spec generator
Table 2: Deliminators
| Deliminator | Examples | Test 1 |  |  | Test 2 |  |  | Test 3
|  |  | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3
| , | [100, 200, 300] | 100 | 200 | 300
| ; | 100; 200; 300 | 100 |  |  | 200 |  |  | 300
| : | 100:300 (steps = 100) | 100 |  |  | 200 |  |  | 300
| In general, if a test is specified as (In the Config_test workbook sheet): |  | Col1 | Col2
|  |  | 23; 67 | 122; 215
| Then the following tests are produced (In the runner_spec.csv): |  |  | Col1 | Col2
|  |  | Test1 | 23 | 122
|  |  | Test2 | 23 | 215
|  |  | Test3 | 67 | 122
|  |  | Test4 | 67 | 215
| However, in the case of SCR=POC and X/R=POC we get the following: |  |  | SCR | X/R
|  |  | Test1 | POC SCR low | POC X/R low
|  |  | Test2 | POC SCR high | POC X/R high
4) Figure Profiles
- | Default profiles in the "Figure References" tab SHOULD REMAIN CONSTANT, only change if they are not an appropriate model for the DMAT (or other test) in accordance
- | To make a minor change to an existing default profile, ensure that the delta, timestep, ramp values are changed in alignment (equal number of elements)
- | To make a fresh profile, make a new row of the profile under "Figure References"and fill in the delta, timestep and ramp columns as needed.
Profiles
For signals which change over time, these can reference Figure references which contain some default profiles, or a custom one can be added. It is important to correctly understand how a profile will be specified.
An example from DMAT 3.2.14 is shown below. Consider the profile in red.
[5 empty] | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false] |  | Time Step | Delta | Absolute
[5 empty] | Time Step | Delta | Ramp |  | 0 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 5 | 0 | 1
[5 empty] | 5 | -0.9 | FALSE | => | 5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | FALSE |  | 5.5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | TRUE |  | 5.5 | -0.2 | 0.8
[5 empty] | 6.5 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[5 empty] | 12 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[9 empty] | 6.5 | 0 | 1
[9 empty] | 6.5 | 0 | 1
[9 empty] | 12 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 0 | 0
[5 empty] | 3 | 0 | TRUE |  | 3 | 0
[5 empty] | 3.5 | -2 | FALSE |  | 3 | 0
[5 empty] | 15 | -2 | FALSE |  | 3.5 | -2
[9 empty] | 3.5 | -2
[9 empty] | 15 | -2

## Figure References
Suite | Type | Figure | Time Steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.3,-0.3,0,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.95,0,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,0,2,2,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-3,0,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,0,-3,-3,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,0,-0.1,-0.1,0.1,0.1,-0.1,-0.1,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.1,0.1,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.5,5.5,6.5,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.5,5.5,6.5,12] | [0,-0.5,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip80 | [0,5,5.5,6.5,12] | [0,-0.2,-0.2,0,0] | [false,false,true,false,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1,1] | [false,false,false,false,false,false,false,false]

## Checklist
Checklist | Action
Flat Run | Yes
Snapshot | Yes
Balanced Fault | Yes
Unbalanced Fault | Yes
MFRT | Yes
Temporary Over Voltage | Yes
Voltage Reference Step Change | Yes
Active Power Reference Step | Yes
Grid Frequency | Yes
Grid Voltage Change | Yes
Grid Oscillation Rejection | Yes
Grid Voltage Phase Angle Change | Yes
SCR1 Active Power Ref Step | Yes
SCR1 FRT | Yes
Site specific SCR FRT | Yes

## Flat Run
Test Name | Test Number | End Run (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | Voltage POC (pu) | Action | Software | Suite
3203_0_3 | 0_3 | 301 | enabled | POC; 5 | POC; 6 | 1 | 1.034 | Yes | Both | Reduced_DMAT
3203_0_4 | 0_4 | 301 | disabled | POC; 5 | POC; 6 | 1 | 1.034 | No | PSCAD | Reduced_DMAT
3203_0_5 | 0_5 | 301 | enabled | POC; 5 | POC; 6 | 0.05 | 1.034 | Yes | Both | Reduced_DMAT
3203_0_6 | 0_6 | 5 | enabled | POC; 10 | POC; 6 | 1 | 1.034 | No | Both | Reduced_DMAT
3203_0_7 | 0_7 | 5 | enabled | POC; 3 | POC; 6 | 1 | 1.034 | No | Both | DMAT

## Snapshot
Test Name | Test Number | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Suite | Software
3203_0_1 | 0_1 | 5 | 3 | 10 | 6 | 1 | Yes | Reduced_DMAT | PSCAD
3203_0_2 | 0_2 | 5 | 3 | 3 | 6 | 1 | Yes | DMAT | PSCAD

## Balanced Fault
Test Name | Test Number | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
3204_1 | 1 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
3204_2 | 2 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Both | DMAT
3204_3 | 3 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Both | DMAT
3204_4 | 4 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Both | DMAT
3204_5 | 5 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | Both | DMAT
3204_6 | 6 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Both | DMAT
3204_7 | 7 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Both | DMAT
3204_8 | 8 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
3204_9 | 9 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
3204_10 | 10 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Both | DMAT
3204_11 | 11 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
3204_12 | 12 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
3204_13 | 13 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | Both | DMAT
3204_14 | 14 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Both | DMAT
3204_15 | 15 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Both | DMAT
3204_16 | 16 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Both | DMAT
3204_17 | 17 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Both | DMAT
3204_18 | 18 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Both | DMAT
3204_19 | 19 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Both | DMAT
3204_20 | 20 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
3204_21 | 21 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
3204_22 | 22 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Both | DMAT
3204_23 | 23 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
3204_24 | 24 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
3204_25 | 25 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | 0 | Yes | Both | DMAT
3204_26 | 26 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | -0.3 | No | Both | DMAT
3204_27 | 27 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | 0.3 | No | Both | DMAT
3204_28 | 28 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 14 | 1 | 0 | No | Both | DMAT
3204_29 | 29 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 1 | -0.3 | No | Both | DMAT
3204_30 | 30 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 1 | 0.3 | No | Both | DMAT
3204_31 | 31 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | 0 | No | Both | DMAT
3204_32 | 32 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
3204_33 | 33 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
3204_34 | 34 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 14 | 0.05 | 0 | No | Both | DMAT
3204_35 | 35 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
3204_36 | 36 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT

## Unbalanced Fault
Test Name | Test Number | Fault Duration (s) | End Run (s) | Apply Fault (s) | Fault Type | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3205_37 | 37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_37 | 37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
3205_38 | 38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_39 | 39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_40 | 40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_41 | 41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_42 | 42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_43 | 43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_43 | 43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
3205_44 | 44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_45 | 45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_46 | 46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_47 | 47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_48 | 48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_49 | 49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_49 | 49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3205_50 | 50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_51 | 51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_52 | 52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_53 | 53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_54 | 54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_55 | 55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_55 | 55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
3205_56 | 56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_57 | 57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_58 | 58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_59 | 59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_60 | 60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_61 | 61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_61 | 61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3205_62 | 62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_63 | 63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_64 | 64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_65 | 65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_66 | 66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_67 | 67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_67 | 67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
3205_68 | 68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_69 | 69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_70 | 70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_71 | 71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_72 | 72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_73 | 73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_73 | 73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3205_74 | 74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_75 | 75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_76 | 76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_77 | 77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_78 | 78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_79 | 79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_79 | 79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
3205_80 | 80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_81 | 81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_82 | 82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_83 | 83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_84 | 84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_85 | 85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_85 | 85-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3205_86 | 86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_87 | 87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_88 | 88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_89 | 89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_90 | 90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_91 | 91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_91 | 91-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
3205_92 | 92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_93 | 93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_94 | 94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_95 | 95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_96 | 96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_97 | 97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | Yes | DMAT | PSCAD
3205_97 | 97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | DMAT | PSCAD
3205_98 | 98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_99 | 99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_100 | 100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_101 | 101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_102 | 102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_103 | 103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_103 | 103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
3205_104 | 104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_105 | 105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_106 | 106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_107 | 107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_108 | 108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_109 | 109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_109 | 109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | DMAT | PSCAD
3205_110 | 110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3205_111 | 111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3205_112 | 112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3205_113 | 113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3205_114 | 114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3205_115 | 115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_115 | 115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
3205_116 | 116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_117 | 117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
3205_118 | 118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
3205_119 | 119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
3205_120 | 120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD

## MFRT
Test Name | Test Number | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
3206_121 | 121 | 60 | 5 | S1 | 0.25 | POC | POC | 1 | 0 | No | PSCAD | Reduced_DMAT
3206_122 | 122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | No | PSCAD | Reduced_DMAT
3206_123 | 123 | 60 | 5 | S3 | S3 | POC | POC | 1 | 0 | No | PSCAD | DMAT
3206_124 | 124 | 60 | 5 | S4 | S4 | POC | POC | 1 | 0 | No | PSCAD | DMAT
3206_125 | 125 | 60 | 5 | S5 | S5 | POC | POC | 1 | 0 | Yes | PSCAD | DMAT
3207_126 | 126 | 60 | 5 | P1 | P1 | POC | POC | 1 | 0 | No | PSSE | Reduced_DMAT
3207_127 | 127 | 60 | 5 | P2 | P2 | POC | POC | 1 | 0 | No | PSSE | Reduced_DMAT
3207_128 | 128 | 60 | 5 | P3 | P3 | POC | POC | 1 | 0 | No | PSSE | DMAT
3207_129 | 129 | 60 | 5 | P4 | P4 | POC | POC | 1 | 0 | No | PSSE | DMAT
3207_130 | 130 | 60 | 5 | P5 | P5 | POC | POC | 1 | 0 | No | PSSE | DMAT

## Temporary Over Voltage
Test Name | Test Number | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3209_131 | 131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | DMAT | PSCAD
3209_132 | 132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | DMAT | PSCAD
3209_133 | 133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3209_134 | 134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3209_135 | 135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3209_136 | 136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3209_137 | 137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3209_138 | 138 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | No | DMAT | PSCAD
3209_139 | 139 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | No | DMAT | PSCAD
3209_140 | 140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
3209_141 | 141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
3209_142 | 142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
3209_143 | 143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
3209_144 | 144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
3209_145 | 145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
3209_146 | 146 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3209_147 | 147 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | No | DMAT | PSCAD
3209_148 | 148 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | No | DMAT | PSCAD

## Voltage Reference Step Change
Test Name | Test Number | End Run (s) | Event | Time Steps (s) | Delta (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Suite | Software
3210_149 | 149 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
3210_150 | 150 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
3210_151 | 151 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3210_152 | 152 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3210_153 | 153 | 45 | Vref | fig2 | fig2 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3210_154 | 154 | 45 | Vref | fig2 | fig2 | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
3210_155 | 155 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3210_156 | 156 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3210_157 | 157 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3210_158 | 158 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3210_159 | 159 | 45 | Vgrid | fig3 | fig3 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3210_160 | 160 | 45 | Vgrid | fig3 | fig3 | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
3210_161 | 161 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3210_162 | 162 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3210_163 | 163 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3210_164 | 164 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3210_165 | 165 | 45 | Qref | fig4 | fig4 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3210_166 | 166 | 45 | Qref | fig4 | fig4 | POC | POC | 0.05 | 0 | No | DMAT | PSCAD

## Active Power Reference Step
Test Name | Test Number | End Run (s) | SCR | X/R | Time Steps (s) | Pref Deltas (pu) | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3211_167 | 167 | 35 | 10 | 14 | fig5 | fig5 | 1 | 0 | Yes | DMAT | PSCAD
3211_168 | 168 | 35 | 3 | 14 | fig5 | fig5 | 1 | 0 | Yes | DMAT | PSCAD
3211_169 | 169 | 35 | POC | POC | fig5 | fig5 | 1 | 0 | No | Reduced_DMAT | PSCAD

## Grid Frequency
Test Name | Test Number | End Run (s) | Time Steps (s) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
3212_170 | 170 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
3212_171 | 171 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3212_172 | 172 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3212_173 | 173 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.05 | 0 | No | Both | Reduced_DMAT
3212_174 | 174 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
3212_175 | 175 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3212_176 | 176 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3212_177 | 177 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.05 | 0 | No | Both | Reduced_DMAT

## Grid Voltage Change
Test Name | Test Number | End Run (s) | Time Steps (s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
3214_178 | 178 | 65 | fig8 | fig8 | fig8 | 10 | 14; 3 | 1 | 0 | Yes | Both | DMAT
3214_179 | 179 | 65 | fig8 | fig8 | fig8 | 3 | 14; 3 | 1 | 0 | Yes | Both | DMAT
3214_180 | 180 | 65 | fig8 | fig8 | fig8 | POC | POC | 1 | 0 | No | Both | Reduced_DMAT
3214_181 | 181 | 65 | fig8 | fig8 | fig8 | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3214_182 | 182 | 45 | fig9 | fig9 | fig9 | 10 | 14; 3 | 1 | 0 | No | Both | DMAT
3214_183 | 183 | 45 | fig9 | fig9 | fig9 | 3 | 14; 3 | 1 | 0 | No | Both | DMAT
3214_184 | 184 | 45 | fig9 | fig9 | fig9 | POC | POC | 1 | 0 | No | Both | Reduced_DMAT
3214_185 | 185 | 45 | fig9 | fig9 | fig9 | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
3214_186 | 186 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 10 | 14; 3 | 1 | 0 | No | Both | DMAT
3214_187 | 187 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 3 | 14; 3 | 1 | 0 | No | Both | DMAT
3214_188 | 188 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 1 | 0 | No | Both | Reduced_DMAT
3214_189 | 189 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT

## Grid Oscillation Rejection
Test Name | Test Number | End Run (s) | Time Steps (s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | SCR | X/R | Osc Phase (deg) | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3215_190 | 190 | 20 | [5,15] | 0.1:0.9 | 0.005 | 0.1 | POC | POC | 0 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
3215_191 | 191 | 20 | [5,15] | 1:45 | 0.005 | 1 | POC | POC | 0 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
3215_192 | 192 | 20 | [5,15] | 0.1:0.9; 1:45 | 0.005 | 0.1; 1 | POC | POC | 2 | 1 | 0 | No | DMAT | PSCAD

## Grid Voltage Phase Angle Change
Test Name | Test Number | End Run (s) | Apply Event (s) | Angle Change (deg) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3216_193 | 193 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
3216_194 | 194 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
3216_195 | 195 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
3216_196 | 196 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3216_197 | 197 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3216_198 | 198 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 0.05 | 0 | No | DMAT | PSCAD

## SCR1 Active Power Ref Step
Test Name | Test Number | Time Steps (s) | Pref Deltas (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | End Run (s) | Suite | Software
3217_199 | 199 | fig12 | fig12 | 1 | 14; 3 | 0.05 | 0 | Yes | 30 | Reduced_DMAT | PSCAD

## SCR1 FRT
Test Name | Test Number | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3218_200 | 200 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
3218_201 | 201 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 0.5 | 0 | Yes | DMAT | PSCAD
3218_202 | 202 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
3218_203 | 203 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 1 | 0 | No | Reduced_DMAT | PSCAD
3218_204 | 204 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 0.5 | 0 | No | DMAT | PSCAD
3218_205 | 205 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD

## Site specific SCR FRT
Test Name | Test Number | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
3219_206 | 206 | 8 | 5 | 0.43 | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_207 | 207 | 8 | 5 | 0.43 | Zf=0.11xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_208 | 208 | 8 | 5 | 0.43 | Zf=0.25xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_209 | 209 | 8 | 5 | 0.43 | Zf=0.42xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_210 | 210 | 8 | 5 | 0.43 | Zf=0.66xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_211 | 211 | 8 | 5 | 0.43 | Zf=1xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_212 | 212 | 8 | 5 | 0.43 | Zf=1.5xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_213 | 213 | 8 | 5 | 0.43 | Zf=2.3xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_214 | 214 | 8 | 5 | 0.43 | Zf=4xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
3219_215 | 215 | 8 | 5 | 0.43 | Zf=9xZs | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
3219_216 | 216 | 8 | 5 | 0.43 | Zf=0 | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_217 | 217 | 8 | 5 | 0.43 | Zf=0.11xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_218 | 218 | 8 | 5 | 0.43 | Zf=0.25xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_219 | 219 | 8 | 5 | 0.43 | Zf=0.42xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_220 | 220 | 8 | 5 | 0.43 | Zf=0.66xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_221 | 221 | 8 | 5 | 0.43 | Zf=1xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_222 | 222 | 8 | 5 | 0.43 | Zf=1.5xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_223 | 223 | 8 | 5 | 0.43 | Zf=2.3xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_224 | 224 | 8 | 5 | 0.43 | Zf=4xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
3219_225 | 225 | 8 | 5 | 0.43 | Zf=9xZs | POC | POC | 0.5 | 0 | Yes | Reduced_DMAT | PSCAD