## ReadMe
SUMMARY
- This Config_test.xlsx will produce the runner_spec.csv file with the custom selected tests to run for the DMAT and CSR.
- runner_spec.csv is used by run_pscad.py or run_psse.py scripts to run the tests.
TO DO BEFORE RUNNING SCRIPT
1) Ensure correct Suite, Software and WF States are selected in the System_inf tab
2) Ensure correct clauses are selected in the Checklist tab by choosing "Yes" or "No" in the Action column
3) If non suite is selected, for the selected test clause sheets select "Yes" or "No" in the Action column
WORKBOOK INFORMATION
1) Using the "System_inf" tab
- | This sheet is used to specify the parameters for the test sets. The table shows some of the possible inputs.
- | The options in yellow are the common ones to make changes for different run scenarios
| V_POC | Nominal Power | Plant Capacity | Fault level | POC SCR | POC XR ratio | POC base Voltage | Nominal Frequency | Qlead,Qlag | Save Format | Q-V Droop | Suite | Software | WF States | Vgrid | Reference
| 1.034 | 150 | 150 | 901.186 | [12.676303,2.2863071] | [6.66,5.33] | 220 | 50 | [0.3,-0.3] | csv | 0.05 | Run a suite of tests or not | If we want to run tests on PSCAD or PSSE | Describes the wf states which we want to run for. | To select between applying disturbance at either slack bus or using a dummy Tx in PSCAD
[12 empty] | DMAT | PSCAD | ALL | Vslack
[12 empty] | Reduced DMAT | PSSE | WTG PZERO | POC disturbance | Pbase 70, wtg=0
[12 empty] | CSR | Both | BESS PMAX |  | base=150, bess=70
[12 empty] | None |  | BESS PZERO |  | base=150, bess=0
[14 empty] | BESS PMIN |  | base=150, bess=-70
[14 empty] | Pneg, WTG PZERO |  | base=-70, wtg=0
WTG PZERO; BESS PMAX
2) TABLE HEADERS
- | These are already set by default, avoid changing them.
- | Refer to Table 1 for headers of test tables and input options. For the SpecGenerator code to work, it is ESSENTIAL to use the exact header names in Table 1 and input format specified.
- | Every new test sheet created should include the headers under "Must Include" in Table 1
- | Order of headers does not matter
Table 1: (Every sheet must include)
| Info | Test | Action | Software | Suite | End Run (s) | SCR | X/R
| Description: | Test number to be added to the end of the file name. | Manual selection to choose if test will be included in runner_spec | Test for PSSE or PSCAD | Test suite category | Simulation time | Desired Grid SCR Level | Desired Grid X/R
| Options / Exmaples: |  | Yes | PSSE | DMAT | 45 | 12 | 6
|  |  | No | PSCAD | Reduced_DMAT |  | POC | POC
|  |  |  | Both | CSR |  | [12,1]
[5 empty] | None |  | inf | inf
[7 empty] | POC MIN | POC MIN
[7 empty] | POC MAX | POC MAX
WITHSTAND SCR
Table 1a: Optional Headings
| Info | Time Steps (s) | Active Power (pu) | WTG Pref (pu) | BESS Pref (pu) | Pref Deltas (pu) | Pref Ramp (pu/s) | Reactive Power (pu) | Voltage POC (pu) | Voltage POC Deltas (pu) | Voltage POC Ramp (pu/s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Voltage Step (pu) | Vref (pu) | Vref Delta (pu)
| Description: | Time profile for step changes | Wind farm active power reference (applied to BESS or WT depending on WF States from the "System_inf" tab) |  |  | Difference form original P ref at every timestep. |  | Wind farm reactive power setpoint | POC voltage | Difference form original voltage at every timestep. The steps are applied to the Dummy Tx in pscad. | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Difference form original voltage at every timestep. The steps are applied at the slack bus in pscad | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Desired Voltage reference | Difference form original voltage at every timestep. The voltage reference is stepped accordingly
| Options / Exmaples: | [0,5,8] - user defined timesteps | 0.6 |  |  | [0,-0.2,0,0.2,0] - user defined pref_deltas |  | 0.3 | 1.034 | [0,-0.1,0,0.1,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) | 0.1 | 1.034 | Similar to Voltage POC Deltas (pu/s)
|  | fig1 - using a figure from "Figure References" tab for customised profile timesteps | [0, 0.2, 0.4] |  |  | fig1 - using a figure from "Figure References" tab for customised profile pref_deltas |  |  |  | fig1 - using a figure from "Figure References" tab for customised profile voltage deltas | fig1 - using a figure from "Figure References" tab for customised profile voltage ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) |  |  | Similar to Voltage POC Deltas (pu/s)
Table 1b: Optional Headings
| Info | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | Fault X/R | Event | Delta (pu) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | Osc Phase (deg) | Angle Change
| Description: | Time at which a fault is applied | Duration of fault | Fault type | Fault impedance for: - Under voltage faults - Temporary Over Voltage faults (ToV) | Usually matches grid Z, but custom specified for some S5255 tests | Event type if Delta title is used | For a change in value specified in Event, the difference from the original value in pu. | Difference form original freq at every timestep. | Ramp to different freq false/blank - no ramping (infinite step) true - ramp to next value | Grid voltage oscillation frequency | Grid voltage oscillation magntude | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Grid voltage oscillation phase | Grid phase angle change
| Options / Exmaples: | 5 - Single fault applied at time = 5s | 0.25 - Single fault duration | 3PHG | Zf=0 |  | Vref | [0,-0.1,0,0.1,0] - user defined deltas | [0,-1,0,2,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | 0.1 - 0.1Hz oscillation | 0.2 | 0.1 | 2 | 40
|  | [5, 5.5, 6.7] - MFRT | [0.1, 0.1, 0.25] - MFRT | 2PHG | Zf=Zs |  | Vgrid | fig1 - using a figure from "Figure References" tab for customised profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | 0.1:0.9 - Range of oscillations, refer to Table 2 for more info |  |  |  | 40; -40; 60; -60
|  |  | S1 - sequence that defines durations | 1PHG | Zf="K"xZs where K is an integer |  | Qref
|  |  |  | L-L | TOV: Yf = jXc (U_Ov = 1.15pu)
Zf=Rf = 1, 5 and 10 Ohm
S1 -Sequence (MFRT)
3) Test Deliminators
- | The meaning of the general notation of deliminators to differentiate between tests in described
- | Essential to understand when iterating through multiple tests using the spec generator
Table 2: Deliminators
| Deliminator | Examples | Test 1 |  |  | Test 2 |  |  | Test 3
|  |  | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3
| , | [100, 200, 300] | 100 | 200 | 300
| ; | 100; 200; 300 | 100 |  |  | 200 |  |  | 300
| : | 100:300 (steps = 100) | 100 |  |  | 200 |  |  | 300
| In general, if a test is specified as (In the Config_test workbook sheet): |  | Col1 | Col2
|  |  | 23; 67 | 122; 215
| Then the following tests are produced (In the runner_spec.csv): |  |  | Col1 | Col2
|  |  | Test1 | 23 | 122
|  |  | Test2 | 23 | 215
|  |  | Test3 | 67 | 122
|  |  | Test4 | 67 | 215
| However, in the case of SCR=POC and X/R=POC we get the following: |  |  | SCR | X/R
|  |  | Test1 | POC SCR low | POC X/R low
|  |  | Test2 | POC SCR high | POC X/R high
4) Figure Profiles
- | Default profiles in the "Figure References" tab SHOULD REMAIN CONSTANT, only change if they are not an appropriate model for the DMAT (or other test) in accordance
- | To make a minor change to an existing default profile, ensure that the delta, timestep, ramp values are changed in alignment (equal number of elements)
- | To make a fresh profile, make a new row of the profile under "Figure References"and fill in the delta, timestep and ramp columns as needed.
Profiles
For signals which change over time, these can reference Figure references which contain some default profiles, or a custom one can be added. It is important to correctly understand how a profile will be specified.
An example from DMAT 3.2.14 is shown below. Consider the profile in red.
[5 empty] | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false] |  | Time Step | Delta | Absolute
[5 empty] | Time Step | Delta | Ramp |  | 0 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 5 | 0 | 1
[5 empty] | 5 | -0.9 | FALSE | => | 5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | FALSE |  | 5.5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | TRUE |  | 5.5 | -0.2 | 0.8
[5 empty] | 6.5 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[5 empty] | 12 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[9 empty] | 6.5 | 0 | 1
[9 empty] | 6.5 | 0 | 1
[9 empty] | 12 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 0 | 0
[5 empty] | 3 | 0 | TRUE |  | 3 | 0
[5 empty] | 3.5 | -2 | FALSE |  | 3 | 0
[5 empty] | 15 | -2 | FALSE |  | 3.5 | -2
[9 empty] | 3.5 | -2
[9 empty] | 15 | -2

## System_inf
Var name | Var Val | unit
Nominal Voltage | 1.034 | pu
Nominal Active Power | 585 | MW
Nominal Reactive Power | 231.075 | MVAr
Nominal Frequency | 50 | Hz
Plant Capacity | 628.9838 | MVA
BESS Capacity | 200 | MW
POC SCR | [2.2863071,12.676303]
POC XR ratio | [5.33,6.66]
POC Base Voltage | 330 | kV
Q-V Droop | 0.05
Software | PSCAD
WF States | BESS PZERO
Vgrid | POC disturbance
Withstand SCR | 1.5
CSR address | C:\grid_workspace\junction_rivers_stage2\src\junction_rivers_stage2\PSCAD\scripts\Config_CSR_test.xlsx
DMAT address | C:\grid_workspace\junction_rivers_stage2\src\junction_rivers_stage2\PSCAD\scripts\Config_DMAT_test.xlsx
Seperate Spec Sheets | TRUE

## Checklist
Checklist | Action
Page 1 | Yes
Page 2 | Yes

## Figure References
Suite | Type | Figure | Time Steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.3,-0.3,0,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.95,0,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,0,2,2,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-3,0,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,0,-3,-3,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,0,-0.1,-0.1,0.1,0.1,-0.1,-0.1,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.1,0.1,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.5,5.5,6.5,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.5,5.5,6.5,12] | [0,-0.5,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip80 | [0,5,5.5,6.5,12] | [0,-0.2,-0.2,0,0] | [false,false,true,false,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1,1] | [false,false,false,false,false,false,false,false]

## Page 1
Test | Action | Software | Suite | End Run (s) | SCR | X/R | Time Steps (s) | Active Power (pu) | WTG Pref (pu) | BESS Pref (pu) | Pref Deltas (pu) | Pref Ramp (pu/s) | Reactive Power (pu) | Voltage POC (pu) | Voltage POC Deltas (pu) | Voltage POC Ramp (pu/s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Voltage Step (pu) | Vref (pu) | Vref Delta (pu) | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | Fault X/R | Event | Delta (pu) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | Osc Phase (deg) | Angle Change
1 | 10 | POC MIN | POC MIN; POC | 1 | 1.034 | Yes | Both | Reduced_DMAT
2 | 10 | POC MAX; POC | POC MAX | 1 | 1.034 | Yes | PSCAD | Reduced_DMAT
3 | 10 | POC MIN; 6 | POC; 6 | 0.05 | 1.034 | Yes | Both | Reduced_DMAT
4 | 10 | POC; 10 | POC; 6 | 1 | 1.034 | Yes | Both | Reduced_DMAT
5 | 10 | POC; 3 | POC; 6 | 1 | 1.034 | Yes | Both | DMAT
6 | 23 | 4 | 6 | [5 empty] | 1 | 0

## Page 2
Test | Action | Software | Suite | End Run (s) | SCR | X/R | Time Steps (s) | Active Power (pu) | WTG Pref (pu) | BESS Pref (pu) | Pref Deltas (pu) | Pref Ramp (pu/s) | Reactive Power (pu) | Voltage POC (pu) | Voltage POC Deltas (pu) | Voltage POC Ramp (pu/s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Voltage Step (pu) | Vref (pu) | Vref Delta (pu) | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | Fault X/R | Event | Delta (pu) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | Osc Phase (deg) | Angle Change
1 | 10 | POC MIN | POC MIN; POC | 1 | 1.034 | Yes | Both | Reduced_DMAT
2 | 10 | POC MAX; POC | POC MAX | 1 | 1.034 | Yes | PSCAD | Reduced_DMAT
3 | 10 | POC MIN; 6 | POC; 6 | 0.05 | 1.034 | Yes | Both | Reduced_DMAT
4 | 10 | POC; 10 | POC; 6 | 1 | 1.034 | Yes | Both | Reduced_DMAT
5 | 10 | POC; 3 | POC; 6 | 1 | 1.034 | Yes | Both | DMAT
6 | 23 | 4 | 6 | [5 empty] | 1 | 0