## System_inf
Var name | Var Val | unit
Workspacename
CaseName
POC Bus Name | 101
Terminal Bus Name | 102
V_POC | 1.034 | pu
Nominal Power | 150 | MW
Plant Capacity | 150 | MVA
Fault level | 901.186 | MVA
POC SCR | [12.676303,2.2863071]
POC XR ratio | [6.66,5.33]
POC base Voltage | 220 | kV
Nominal Frequency | 50 | Hz
Qlead,Qlag | [0.3,-0.3]
Save Format | csv | out,csv
Time step | 16.6667 | us
Channel plot | 200 | us
Q-V Droop | 0.046657
Suite | DMAT

## PPC_Signals
Signals | Variable | Value
PPC name
Pref
Qref | Qcm
PFref | PFref
Vdroop | Vref
id
iq
Inverter Name
Q_control_mode | Droop
Is Inside module activated? | No
Module Name

## V_droop
Qmax | Qmin | Qnom | P-slope | N-slope | deadband1 | deadband2 | deadband |  | Qbase-Vestas(MW) | Vref | Qoffset | Vmax
118.5 | -118.5 | 0 | 39.5 | 39.5 | 1 | 1 | 0 | 0.04 | 1.975 | 1 | 0 | 1.05

## Checklist
Checklist | Action
Flat Run | Yes
Snapshot | Yes
Balanced Fault | Yes
Unbalanced Fault | Yes
MFRT | Yes
Temporary Over Voltage | Yes
Voltage Reference Step Change | Yes
Active Power Reference Step | Yes
Grid Frequency | Yes
Grid Voltage Change | Yes
Grid Oscillation Rejection | Yes
Grid Voltage Phase Angle Change | Yes
SCR1 Active Power Ref Step | Yes
SCR1 FRT | Yes
Site specific SCR FRT | Yes
CSR_S5251 | Yes
CSR_S5253
CSR_S5254

## Snapshot
Test | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Reduced DMAT | Suite
0.4 | 5 | 3 | 10 | 6 | 1 | Yes | Yes | Reduced DMAT
0.5 | 5 | 3 | 3 | 6 | 1 | No | No | DMAT

## Flat Run
Test | End Run (s) | Time Steps (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | WTG Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
0.1 | 301 |  | enabled | POC; 5 | POC; 6 | 1 |  |  |  |  | Yes | Both | Reduced_DMAT
0.2 | 301 |  | disabled | POC; 5 | POC; 6 | 1 |  |  |  |  | No | PSCAD | Reduced_DMAT
0.3 | 301 |  | enabled | POC; 5 | POC; 6 | 0.05 |  |  |  |  | No | Both | Reduced_DMAT
0.4 | 5 |  | enabled | POC; 10 | POC; 6 | 1 |  |  |  |  | No | Both | Reduced_DMAT
0.5 | 5 |  | enabled | POC; 3 | POC; 6 | 1 |  |  |  |  | No | Both | DMAT

## Balanced Fault
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault type | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Reduced DMAT | Suite
1 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0 | Yes | Both | DMAT | DMAT
2 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | -0.3 | No | Both | DMAT | DMAT
3 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0.3 | No | Both | DMAT | DMAT
4 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 1 | 0 | No | Both | DMAT | DMAT
5 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | -0.3 | No | Both | DMAT | DMAT
6 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | 0.3 | No | Both | DMAT | DMAT
7 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
8 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT | DMAT
9 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT | DMAT
10 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
11 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT | DMAT
12 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT | DMAT
13 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0 | No | Both | DMAT | DMAT
14 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | -0.3 | No | Both | DMAT | DMAT
15 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0.3 | No | Both | DMAT | DMAT
16 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 1 | 0 | No | Both | DMAT | DMAT
17 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | -0.3 | No | Both | DMAT | DMAT
18 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | 0.3 | No | Both | DMAT | DMAT
19 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
20 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT | DMAT
21 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT | DMAT
22 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
23 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT | DMAT
24 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT | DMAT
25 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0 | No | Both | DMAT | DMAT
26 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | -0.3 | No | Both | DMAT | DMAT
27 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0.3 | No | Both | DMAT | DMAT
28 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 1 | 0 | No | Both | DMAT | DMAT
29 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | -0.3 | No | Both | DMAT | DMAT
30 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | 0.3 | No | Both | DMAT | DMAT
31 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
32 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT | DMAT
33 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT | DMAT
34 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 0.05 | 0 | No | Both | DMAT | DMAT
35 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT | DMAT
36 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT | DMAT

## Unbalanced Fault
Test | Fault duration (s) | End Run (s) | Apply fault (s) | Fault type | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Action2 | Reduced DMAT | Suite
37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | Yes | No | DMAT
37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | DMAT
38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | DMAT
44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | Yes | No | DMAT
49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes | Yes | DMAT
50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes | Yes | DMAT
56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | Yes | No | DMAT
61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | DMAT
62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | DMAT
68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | Yes | No | DMAT
73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes | Yes | DMAT
74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes | Yes | DMAT
80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | Yes | No | DMAT
85-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | DMAT
86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
91-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | DMAT
92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | Yes | Yes | No | DMAT
97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | Yes | No | DMAT
98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | Yes | No | DMAT
104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT
109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | Yes | No | DMAT
109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | Yes | No | DMAT
110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | Yes | No | DMAT
111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | Yes | No | DMAT
112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | Yes | No | DMAT
113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | Yes | No | DMAT
114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | Yes | No | DMAT
115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | Yes | No | DMAT
115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | Yes | No | DMAT
116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | Yes | No | DMAT
117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | Yes | No | DMAT
118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | Yes | No | DMAT
119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | Yes | No | DMAT
120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | Yes | No | DMAT

## Temporary Over Voltage
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | No | DMAT
132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | No | No | DMAT
133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | No | No | DMAT
134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | No | No | DMAT
135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | No | No | DMAT
136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | No | No | DMAT
137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | No | Yes | DMAT
138 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | No | No | DMAT
139 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | No | No | DMAT
140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | No | No | DMAT
141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | No | No | DMAT
142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | No | No | DMAT
143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | No | No | DMAT
144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | No | No | DMAT
145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | No | No | DMAT
146 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | No | Yes | DMAT
147 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | No | No | DMAT
148 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | No | No | DMAT

## MFRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Software | Suite
121 | 60 | 5 | S1 | 0.25 | POC | POC | 1 | 0 | Yes | Yes | PSCAD | DMAT
122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | No | Yes | PSCAD | DMAT
123 | 60 | 5 | S3 | S3 | POC | POC | 1 | 0 | No | No | PSCAD | DMAT
124 | 60 | 5 | S4 | S4 | POC | POC | 1 | 0 | No | No | PSCAD | DMAT
125 | 60 | 5 | S5 | S5 | POC | POC | 1 | 0 | No | No | PSCAD | DMAT

## Voltage Reference Step Change
Test | End Run (s) | Event | Time Steps (s) | Delta (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT | Suite
149 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 1 | 0 | Yes | No | DMAT
150 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 0.05 | 0 | No | No | DMAT
151 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 1 | 0 | No | No | DMAT
152 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 0.05 | 0 | No | No | DMAT
153 | 45 | Vref | fig2 | fig2 | POC | POC | 1 | 0 | No | Yes | DMAT
154 | 45 | Vref | fig2 | fig2 | POC | POC | 0.05 | 0 | No | No | DMAT
155 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 1 | 0 | No | No | DMAT
156 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 0.05 | 0 | No | No | DMAT
157 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 1 | 0 | No | No | DMAT
158 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 0.05 | 0 | No | No | DMAT
159 | 45 | Vgrid | fig3 | fig3 | POC | POC | 1 | 0 | No | Yes | DMAT
160 | 45 | Vgrid | fig3 | fig3 | POC | POC | 0.05 | 0 | No | No | DMAT
161 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 1 | 0 | No | No
162 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 0.05 | 0 | No | No
163 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 1 | 0 | No | No
164 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 0.05 | 0 | No | No
165 | 45 | Qref | fig4 | fig4 | POC | POC | 1 | 0 | No | Yes
166 | 45 | Qref | fig4 | fig4 | POC | POC | 0.05 | 0 | No | No

## Active Power Reference Step
Test | End Run (s) | SCR | X/R | Time Steps (s) | Pref_deltas (pu) | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
167 | 35 | 10 | 14 | fig5 | fig5 | 1 | 0 | Yes | No | DMAT
168 | 35 | 3 | 14 | fig5 | fig5 | 1 | 0 | No | No | DMAT
169 | 35 | POC | POC | fig5 | fig5 | 1 | 0 | No | Yes | DMAT

## Grid Frequency
Test | End Run (s) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | SCR | X/R | Available Power (%) | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
170 | 16 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
171 | 16 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 0.5 | 0 |  |  |  |  | No | Both | Reduced_DMAT
172 | 16 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | No | Both | Reduced_DMAT
173 | 16 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | No | Both | Reduced_DMAT
174 | 16 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 1 | 0 |  |  |  |  | No | Both | Reduced_DMAT
175 | 16 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 0.5 | 0 |  |  |  |  | No | Both | Reduced_DMAT
176 | 16 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | No | Both | Reduced_DMAT
177 | 16 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | No | Both | Reduced_DMAT

## Grid Voltage Change
Test | End Run (s) | Time Steps (s) | Volt_delta (pu) | Vpoc ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Qpoc (pu) | Software | Suite | Action
178 | 65 | fig8 | fig8 | fig8 | 10 | 14; 3 | 1 | 0 |  |  |  | Both | DMAT | Yes
179 | 65 | fig8 | fig8 | fig8 | 3 | 14; 4 | 1 | 0 |  |  |  | Both | DMAT | No
180 | 65 | fig8 | fig8 | fig8 | POC | POC | 1 | 0 |  |  |  | Both | Reduced_DMAT | No
181 | 65 | fig8 | fig8 | fig8 | POC | POC | 0.5 | 0 |  |  |  | Both | Reduced_DMAT | No
182 | 45 | fig9 | fig9 | fig9 | 10 | 14; 3 | 1 | 0 |  |  |  | Both | DMAT | No
183 | 65 | fig9 | fig9 | fig9 | 3 | 14; 4 | 1 | 0 |  |  |  | Both | DMAT | No
184 | 65 | fig9 | fig9 | fig9 | POC | POC | 1 | 0 |  |  |  | Both | Reduced_DMAT | No
185 | 65 | fig9 | fig9 | fig9 | POC | POC | 0.5 | 0 |  |  |  | Both | Reduced_DMAT | No
186 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 10 | 14; 3 | 1 | 0 |  |  |  | Both | DMAT | No
187 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 3 | 14; 4 | 1 | 0 |  |  |  | Both | DMAT | No
188 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 1 | 0 |  |  |  | Both | Reduced_DMAT | No
189 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 0.5 | 0 |  |  |  | Both | Reduced_DMAT | No

## Grid Oscillation Rejection
Test | End Run (s) | Time Steps (s) | Osc_freq | Magnitude | Step (Hz) | SCR | X/R | Osc_Phase_deg | Active Power (pu) | Reactive Power | Action | Reduced DMAT | Suite
190 | 20 | [5,15] | 0.1:0.9 | 0.005 | 0.1 | POC | POC | 0 | 1 | 0 | Yes | Yes | DMAT
191 | 20 | [5,15] | 1:45 | 0.005 | 1 | POC | POC | 0 | 1 | 0 | No | Yes | DMAT
192 | 20 | [5,15] | 0.1:0.9; 1:45 | 0.005 | 0.1; 1 | POC | POC | 2 | 1 | 0 | No | No | DMAT

## Grid Voltage Phase Angle Change
Test | End Run (s) | Apply event (s) | Angle Change | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
193 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 1 | 0 | Yes | No | DMAT
194 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 0.05 | 0 | No | No | DMAT
195 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 1 | 0 | No | No | DMAT
196 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 0.05 | 0 | No | No | DMAT
197 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 1 | 0 | No | Yes | DMAT
198 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 0.05 | 0 | No | No | DMAT

## SCR1 Active Power Ref Step
Test | Time Steps (s) | Pref_deltas (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT | End Run (s) | Suite
199 | fig12 | fig12 | 1 | 14; 3 | 0.05 | 0 | Yes | Yes | 35 | DMAT

## SCR1 FRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Reduced DMAT | Suite
200 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6 | Yes | DMAT
201 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 0.5 | 0 | No | 1.0058 | [1.05,1.05] | 4 | 6 | No | DMAT
202 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 0.05 | 0 | No | 2.0058 | [1.05,1.05] | 4 | 6 | No | DMAT
203 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 1 | 0 | No | 3.0058 | [1.05,1.05] | 4 | 6 | Yes | DMAT
204 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 0.5 | 0 | No | 1.0839 | [1.05,1.05] | 4 | 6 | No | DMAT
205 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 0.05 | 0 | No | 1.0058 | [1.05,1.05] | 4 | 6 | No | DMAT

## Site specific SCR FRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Retain voltage method | Tx_Tap | Xmin | Xmax | Reduced DMAT | Suite
206 | 8 | 5 | 0.43 | Zf=0 | ~0 | POC | POC | 1 | 0 | Yes | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
207 | 8 | 5 | 0.43 | Zf=0.11xZs | ~0.1 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
208 | 8 | 5 | 0.43 | Zf=0.25xZs | ~0.2 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
209 | 8 | 5 | 0.43 | Zf=0.42xZs | ~0.3 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
210 | 8 | 5 | 0.43 | Zf=0.66xZs | ~0.4 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
211 | 8 | 5 | 0.43 | Zf=1xZs | ~0.5 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
212 | 8 | 5 | 0.43 | Zf=1.5xZs | ~0.6 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
213 | 8 | 5 | 0.43 | Zf=2.3xZs | ~0.7 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
214 | 8 | 5 | 0.43 | Zf=4xZs | ~0.8 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
215 | 8 | 5 | 0.43 | Zf=9xZs | ~0.9 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
216 | 8 | 5 | 0.43 | Zf=0 | 0 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
217 | 8 | 5 | 0.43 | Zf=0.11xZs | ~0.1 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
218 | 8 | 5 | 0.43 | Zf=0.25xZs | ~0.2 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
219 | 8 | 5 | 0.43 | Zf=0.42xZs | ~0.3 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
220 | 8 | 5 | 0.43 | Zf=0.66xZs | ~0.4 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
221 | 8 | 5 | 0.43 | Zf=1xZs | ~0.5 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
222 | 8 | 5 | 0.43 | Zf=1.5xZs | ~0.6 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
223 | 8 | 5 | 0.43 | Zf=2.3xZs | ~0.7 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
224 | 8 | 5 | 0.43 | Zf=4xZs | ~0.8 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT
225 | 8 | 5 | 0.43 | Zf=9xZs | ~0.9 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | DMAT

## Figure References
Suite | Type | Figure | Time_steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.3,-0.3,0,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.95,0,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,2,2,0,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-30,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,-3,-3,0,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,-0.1,-0.1,0.1,0.1,-0.1,-0.1,0,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.1,0.1,0,0] | [false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.5,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip80 | [0,5,5.5,12] | [0,-0.2,0,0] | [false,false,true,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1,1] | [false,false,false,false,false,false,false,false]

## CSR_S5251
Test | End Run (s) | Time Steps (s) | Vpoc_delta (pu) | Ramp/Step | SCR | X/R | WTG Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
csr_s5251_1 | 20 |  |  |  | POC | POC | 1 | 0 | 0.9 | -1 | Yes | Both | CSR
csr_s5251_2 | 20 |  |  |  | POC | POC | 1 | 0 | 0.9 | 0 | Yes | Both | CSR
csr_s5251_3 | 20 |  |  |  | POC | POC | 1 | 0 | 0.9 | 1 | Yes | Both | CSR
csr_s5251_4 | 20 |  |  |  | POC | POC | 1 | 0 | 1.1 | -1 | Yes | Both | CSR
csr_s5251_5 | 20 |  |  |  | POC | POC | 1 | 0 | 1.1 | 0 | Yes | Both | CSR
csr_s5251_6 | 20 |  |  |  | POC | POC | 1 | 0 | 1.1 | 1 | Yes | Both | CSR
csr_s5251_7 | 20 |  |  |  | POC | POC | 1 | -1 | 0.9 | -1 | Yes | Both | CSR
csr_s5251_8 | 20 |  |  |  | POC | POC | 1 | -1 | 0.9 | 0 | Yes | Both | CSR
csr_s5251_9 | 20 |  |  |  | POC | POC | 1 | -1 | 0.9 | 1 | Yes | Both | CSR
csr_s5251_10 | 20 |  |  |  | POC | POC | 1 | -1 | 1.1 | -1 | Yes | Both | CSR
csr_s5251_11 | 20 |  |  |  | POC | POC | 1 | -1 | 1.1 | 0 | Yes | Both | CSR
csr_s5251_12 | 20 |  |  |  | POC | POC | 1 | -1 | 1.1 | 1 | Yes | Both | CSR
csr_s5251_13 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 0.9 | -1 | Yes | Both | CSR
csr_s5251_14 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 0.9 | 0 | Yes | Both | CSR
csr_s5251_15 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 0.9 | 1 | Yes | Both | CSR
csr_s5251_16 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 1.1 | -1 | Yes | Both | CSR
csr_s5251_17 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 1.1 | 0 | Yes | Both | CSR
csr_s5251_18 | 20 |  |  |  | POC | POC | 0.53333 | 1 | 1.1 | 1 | Yes | Both | CSR
csr_s5251_19 | 20 |  |  |  | POC | POC | 0 | 1 | 0.9 | -1 | Yes | Both | CSR
csr_s5251_20 | 20 |  |  |  | POC | POC | 0 | 1 | 0.9 | 0 | Yes | Both | CSR
csr_s5251_21 | 20 |  |  |  | POC | POC | 0 | 1 | 0.9 | 1 | Yes | Both | CSR
csr_s5251_22 | 20 |  |  |  | POC | POC | 0 | 1 | 1.1 | -1 | Yes | Both | CSR
csr_s5251_23 | 20 |  |  |  | POC | POC | 0 | 1 | 1.1 | 0 | Yes | Both | CSR
csr_s5251_24 | 20 |  |  |  | POC | POC | 0 | 1 | 1.1 | 1 | Yes | Both | CSR
csr_s5251_25 | 20 |  |  |  | POC | POC | 0 | -1 | 0.9 | -1 | Yes | Both | CSR
csr_s5251_26 | 20 |  |  |  | POC | POC | 0 | -1 | 0.9 | 0 | Yes | Both | CSR
csr_s5251_27 | 20 |  |  |  | POC | POC | 0 | -1 | 0.9 | 1 | Yes | Both | CSR
csr_s5251_28 | 20 |  |  |  | POC | POC | 0 | -1 | 1.1 | -1 | Yes | Both | CSR
csr_s5251_29 | 20 |  |  |  | POC | POC | 0 | -1 | 1.1 | 0 | Yes | Both | CSR
csr_s5251_30 | 20 |  |  |  | POC | POC | 0 | -1 | 1.1 | 1 | Yes | Both | CSR
csr_s5251_31 | 20 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | inf | inf | 1 | 0 | 1.034 | -1 | Yes | Both | CSR
csr_s5251_32 | 20 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | inf | inf | 0 | -1 | 1.034 | -1 | Yes | Both | CSR
csr_s5251_33 | 22 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | inf | inf | 1 | 0 | 1.034 | 1 | Yes | Both | CSR
csr_s5251_34 | 22 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | inf | inf | 0 | -1 | 1.034 | 1 | Yes | Both | CSR

## CSR_S5253
Test | End Run (s) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
csr_s5253_1 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_2 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_3 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_4 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_5 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_6 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_7 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_8 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_9 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_10 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_11 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_12 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_13 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_14 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_15 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_16 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_17 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_18 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_19 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_20 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_21 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_22 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_23 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_24 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_25 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_26 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_27 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_28 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_29 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_30 | 120 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_31 | 120 | [0,3,3.25,3.9167,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_32 | 120 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_33 | 600 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_34 | 1200 | [0,3,3.25,3.9167,1200] | [0,-1,0,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_35 | 1200 | [0,3,3.125,3.9167,120] | [0,-0.5,0,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_36 | 1200 | [0,3,3.125,3.9167,120] | [0,0.5,0,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_37 | 600 | [0,3,3.25,3.9167,120] | [0,1,0,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_38 | 120 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_39 | 600 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR

## CSR_S5254
Test | End Run (s) | Time Steps (s) | Vpoc_delta (pu) | Ramp/Step | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vref (pu) | Qpoc (pu) | Software | Suite
csr_s5254_1 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_2 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_3 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_4 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_5 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_6 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_7 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_8 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_9 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_10 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_11 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_12 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_13 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_14 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_15 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_16 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_17 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_18 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_19 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_20 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_21 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_22 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_23 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_24 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_25 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_26 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_27 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_28 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_29 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_30 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_31 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_32 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_33 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_34 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_35 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_36 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_37 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_38 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_39 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_40 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_41 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_42 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_43 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_44 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_45 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_46 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_47 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_48 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_49 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_50 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_51 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_52 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_53 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_54 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_55 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_56 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_57 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_58 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_59 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_60 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_61 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_62 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_63 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_64 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_65 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_66 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_67 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_68 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_69 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_70 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_71 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_72 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_73 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_74 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_75 | 60 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_61 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_62 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_63 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_64 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_65 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_66 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_67 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_68 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_69 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_70 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_71 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_72 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_73 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_74 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_75 | 60 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_61 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_62 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_63 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_64 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_65 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_66 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_67 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_68 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_69 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0.53333 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_70 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_71 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_72 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_73 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_74 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_75 | 60 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | inf | inf | 0 | -1 | 1.084 | -1 | PSCAD | CSR

## CSR_S5255
category (delete later) | Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault type | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Column1 | Action | Software | Reduced DMAT
balanced | csr_s5255_1 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC | 1 | 0 |  |  | Yes | Both | DMAT
balanced | csr_s5255_2 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_3 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_4 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_5 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_6 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | Yes | Both | DMAT
balanced | csr_s5255_7 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_8 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_9 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_10 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_11 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_12 | 10 | 5 | 0.43 | 7 | Zf=0 | ~0.0001 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_13 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_14 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_15 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_16 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_17 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_18 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_19 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_20 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_21 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_22 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_23 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_24 | 10 | 5 | 0.43 | 7 | Zf=Zs | ~0.5 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_25 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_26 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_27 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_28 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_29 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_30 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_31 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_32 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_33 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_34 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_35 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT
balanced | csr_s5255_36 | 10 | 5 | 0.5 | 7 | Zf=2xZs | ~0.7 | POC | POC |  |  |  |  | No | Both | DMAT