## ReadMe
SUMMARY
- This Config_test.xlsx will produce the runner_spec.csv file with the custom selected tests to run for the DMAT and CSR.
- runner_spec.csv is used by run_pscad.py or run_psse.py scripts to run the tests.
TO DO BEFORE RUNNING SCRIPT
1) Ensure correct Suite, Software and WF States are selected in the System_inf tab
2) Ensure correct clauses are selected in the Checklist tab by choosing "Yes" or "No" in the Action column
3) For the selected test clause sheets select "Yes" or "No" in the Action column
WORKBOOK INFORMATION
1) Using the "System_inf" tab
- | This sheet is used to specify the parameters for the test sets. The table shows some of the possible inputs.
- | The options in yellow are the common ones to make changes for different run scenarios
| V_POC | Nominal Power | Plant Capacity | Fault level | POC SCR | POC XR ratio | POC base Voltage | Nominal Frequency | Qlead,Qlag | Save Format | Q-V Droop | Suite | Software | WF States | Vgrid | Reference
| 1.034 | 150 | 150 | 901.186 | [12.676303,2.2863071] | [6.66,5.33] | 220 | 50 | [0.3,-0.3] | csv | 0.05 | Run a suite of tests or not | If we want to run tests on PSCAD or PSSE | Describes the wf states which we want to run for. | To select between applying disturbance at either slack bus or using a dummy Tx in PSCAD
[12 empty] | DMAT | PSCAD | ALL | Vslack
[12 empty] | Reduced DMAT | PSSE | WTG PZERO | POC disturbance | Pbase 70, wtg=0
[12 empty] | CSR | Both | BESS PMAX |  | base=150, bess=70
[12 empty] | None |  | BESS PZERO |  | base=150, bess=0
[14 empty] | BESS PMIN |  | base=150, bess=-70
[14 empty] | Pneg, WTG PZERO |  | base=-70, wtg=0
WTG PZERO; BESS PMAX
2) TABLE HEADERS
- | These are already set by default, avoid changing them.
- | Refer to Table 1 for headers of test tables and input options. For the SpecGenerator code to work, it is ESSENTIAL to use the exact header names in Table 1 and input format specified.
- | Every new test sheet created should include the headers under "Must Include" in Table 1
- | Order of headers does not matter
Table 1: (Every sheet must include)
| Info | Test | Action | Software | Suite | End Run (s) | SCR | X/R
| Description: | Test number to be added to the end of the file name. | Manual selection to choose if test will be included in runner_spec | Test for PSSE or PSCAD | Test suite category | Simulation time | Desired Grid SCR Level | Desired Grid X/R
| Options / Exmaples: |  | Yes | PSSE | DMAT | 45 | 12 | 6
|  |  | No | PSCAD | Reduced_DMAT |  | POC | POC
|  |  |  | Both | CSR |  | [12,1]
[5 empty] | None |  | inf | inf
[7 empty] | POC MIN | POC MIN
[7 empty] | POC MAX | POC MAX
Table 1a: Optional Headings
| Info | Time Steps (s) | Active Power (pu) | WTG Pref (pu) | BESS Pref (pu) | Pref Deltas (pu) | Pref Ramp (pu/s) | Reactive Power (pu) | Voltage POC (pu) | Voltage POC Deltas (pu) | Voltage POC Ramp (pu/s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Voltage Step (pu) | Vref (pu) | Vref Delta (pu)
| Description: | Time profile for step changes | Wind farm active power reference (applied to BESS or WT depending on WF States from the "System_inf" tab) |  |  | Difference form original P ref at every timestep. |  | Wind farm reactive power setpoint | POC voltage | Difference form original voltage at every timestep. The steps are applied to the Dummy Tx in pscad. | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Difference form original voltage at every timestep. The steps are applied at the slack bus in pscad | Ramp to different poc voltages false/blank - no ramping (infinite step) true - ramp to next value | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Desired Voltage reference | Difference form original voltage at every timestep. The voltage reference is stepped accordingly
| Options / Exmaples: | [0,5,8] - user defined timesteps | 0.6 |  |  | [0,-0.2,0,0.2,0] - user defined pref_deltas |  | 0.3 | 1.034 | [0,-0.1,0,0.1,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) | 0.1 | 1.034 | Similar to Voltage POC Deltas (pu/s)
|  | fig1 - using a figure from "Figure References" tab for customised profile timesteps | [0, 0.2, 0.4] |  |  | fig1 - using a figure from "Figure References" tab for customised profile pref_deltas |  |  |  | fig1 - using a figure from "Figure References" tab for customised profile voltage deltas | fig1 - using a figure from "Figure References" tab for customised profile voltage ramps | Similar to Voltage POC Deltas (pu/s) | Similar to Voltage POC Ramp (pu/s) |  |  | Similar to Voltage POC Deltas (pu/s)
Table 1b: Optional Headings
| Info | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | Fault X/R | Event | Delta (pu) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | Osc Phase (deg) | Angle Change
| Description: | Time at which a fault is applied | Duration of fault | Fault type | Fault impedance for: - Under voltage faults - Temporary Over Voltage faults (ToV) | Usually matches grid Z, but custom specified for some S5255 tests | Event type if Delta title is used | For a change in value specified in Event, the difference from the original value in pu. | Difference form original freq at every timestep. | Ramp to different freq false/blank - no ramping (infinite step) true - ramp to next value | Grid voltage oscillation frequency | Grid voltage oscillation magntude | Step value when action needs to occur for every iteration in range, ref to Table 2 for more info | Grid voltage oscillation phase | Grid phase angle change
| Options / Exmaples: | 5 - Single fault applied at time = 5s | 0.25 - Single fault duration | 3PHG | Zf=0 |  | Vref | [0,-0.1,0,0.1,0] - user defined deltas | [0,-1,0,2,0] - user defined deltas | [false, true, false, true, false] - user defined ramps | 0.1 - 0.1Hz oscillation | 0.2 | 0.1 | 2 | 40
|  | [5, 5.5, 6.7] - MFRT | [0.1, 0.1, 0.25] - MFRT | 2PHG | Zf=Zs |  | Vgrid | fig1 - using a figure from "Figure References" tab for customised profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | fig1 - using a figure from "Figure References" tab for customised frequency profile deltas | 0.1:0.9 - Range of oscillations, refer to Table 2 for more info |  |  |  | 40; -40; 60; -60
|  |  | S1 - sequence that defines durations | 1PHG | Zf="K"xZs where K is an integer |  | Qref
|  |  |  | L-L | TOV: Yf = jXc (U_Ov = 1.15pu)
Zf=Rf = 1, 5 and 10 Ohm
S1 -Sequence (MFRT)
3) Test Deliminators
- | The meaning of the general notation of deliminators to differentiate between tests in described
- | Essential to understand when iterating through multiple tests using the spec generator
Table 2: Deliminators
| Deliminator | Examples | Test 1 |  |  | Test 2 |  |  | Test 3
|  |  | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3 | Time step 1 | Time step 2 | Time step 3
| , | [100, 200, 300] | 100 | 200 | 300
| ; | 100; 200; 300 | 100 |  |  | 200 |  |  | 300
| : | 100:300 (steps = 100) | 100 |  |  | 200 |  |  | 300
| In general, if a test is specified as (In the Config_test workbook sheet): |  | Col1 | Col2
|  |  | 23; 67 | 122; 215
| Then the following tests are produced (In the runner_spec.csv): |  |  | Col1 | Col2
|  |  | Test1 | 23 | 122
|  |  | Test2 | 23 | 215
|  |  | Test3 | 67 | 122
|  |  | Test4 | 67 | 215
| However, in the case of SCR=POC and X/R=POC we get the following: |  |  | SCR | X/R
|  |  | Test1 | POC SCR low | POC X/R low
|  |  | Test2 | POC SCR high | POC X/R high
4) Figure Profiles
- | Default profiles in the "Figure References" tab SHOULD REMAIN CONSTANT, only change if they are not an appropriate model for the DMAT (or other test) in accordance
- | To make a minor change to an existing default profile, ensure that the delta, timestep, ramp values are changed in alignment (equal number of elements)
- | To make a fresh profile, make a new row of the profile under "Figure References"and fill in the delta, timestep and ramp columns as needed.
Profiles
For signals which change over time, these can reference Figure references which contain some default profiles, or a custom one can be added. It is important to correctly understand how a profile will be specified.
An example from DMAT 3.2.14 is shown below. Consider the profile in red.
[5 empty] | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false] |  | Time Step | Delta | Absolute
[5 empty] | Time Step | Delta | Ramp |  | 0 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 5 | 0 | 1
[5 empty] | 5 | -0.9 | FALSE | => | 5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | FALSE |  | 5.5 | -0.9 | 0.1
[5 empty] | 5.5 | -0.2 | TRUE |  | 5.5 | -0.2 | 0.8
[5 empty] | 6.5 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[5 empty] | 12 | 0 | FALSE |  | 5.5 | -0.2 | 0.8
[9 empty] | 6.5 | 0 | 1
[9 empty] | 6.5 | 0 | 1
[9 empty] | 12 | 0 | 1
[5 empty] | 0 | 0 | FALSE |  | 0 | 0
[5 empty] | 3 | 0 | TRUE |  | 3 | 0
[5 empty] | 3.5 | -2 | FALSE |  | 3 | 0
[5 empty] | 15 | -2 | FALSE |  | 3.5 | -2
[9 empty] | 3.5 | -2
[9 empty] | 15 | -2

## System_inf
Var name | Var Val | unit
Nominal Voltage | 1.034 | pu
Nominal Active Power | 585 | MW
Nominal Reactive Power | 231.075 | MVAr
Nominal Frequency | 50 | Hz
Plant Capacity | 628.9838 | MVA
BESS Capacity | 200 | MW
POC SCR | [2.2863071,12.676303]
POC XR ratio | [5.33,6.66]
POC Base Voltage | 220 | kV
Q-V Droop | 0.05
Suite | None
Software | PSCAD
WF States | BESS PZERO
Vgrid | POC disturbance

## Checklist
Checklist | Action | Column1
Flat Run | Yes
Snapshot | No
Balanced Fault | Yes
Unbalanced Fault | Yes
MFRT | No
Temporary Over Voltage | No
Voltage Reference Step Change | No
Active Power Reference Step | No
Grid Frequency | No
Grid Voltage Change | No
Grid Oscillation Rejection | No
Grid Voltage Phase Angle Change | No
SCR1 Active Power Ref Step | No
SCR1 FRT | No
Site specific SCR FRT | No
CSR_S5251 | No
CSR_S5253 | No
CSR_S5254 | No
CSR_S5255 | No
CSR_S52511 | No
CSR_S52512 | No | does not exist
CSR_S52513 | No
CSR_S52514 | No
CSR_S52516 | No
Testing | No

## Figure References
Suite | Type | Figure | Time Steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.3,-0.3,0,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.95,0,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,0,2,2,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-3,0,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,0,-3,-3,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,0,-0.1,-0.1,0.1,0.1,-0.1,-0.1,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.1,0.1,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.5,5.5,6.5,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.5,5.5,6.5,12] | [0,-0.5,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip80 | [0,5,5.5,6.5,12] | [0,-0.2,-0.2,0,0] | [false,false,true,false,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1,1] | [false,false,false,false,false,false,false,false]

## Testing
Test | End Run (s) | SCR | X/R | Active Power (pu) | Voltage POC (pu) | Action | Software | Suite
1 | 10 | POC MIN | POC MIN; POC | 1 | 1.034 | Yes | Both | Reduced_DMAT
2 | 10 | POC MAX; POC | POC MAX | 1 | 1.034 | Yes | PSCAD | Reduced_DMAT
3 | 10 | POC MIN; 6 | POC; 6 | 0.05 | 1.034 | Yes | Both | Reduced_DMAT
4 | 10 | POC; 10 | POC; 6 | 1 | 1.034 | Yes | Both | Reduced_DMAT
5 | 10 | POC; 3 | POC; 6 | 1 | 1.034 | Yes | Both | DMAT

## Snapshot
Test | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Suite | Software
0_1 | 5 | 3 | 10 | 6 | 1 | Yes | Reduced_DMAT | PSCAD
0_2 | 5 | 3 | 3 | 6 | 1 | Yes | DMAT | PSCAD

## Flat Run
Test | End Run (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | Voltage POC (pu) | Action | Software | Suite
0_3 | 301 | enabled | POC; 5 | POC; 6 | 1 | 1.034 | Yes | Both | Reduced_DMAT
0_4 | 301 | disabled | POC; 5 | POC; 6 | 1 | 1.034 | No | PSCAD | Reduced_DMAT
0_5 | 301 | enabled | POC; 5 | POC; 6 | 0.05 | 1.034 | No | Both | Reduced_DMAT
0_6 | 5 | enabled | POC; 10 | POC; 6 | 1 | 1.034 | No | Both | Reduced_DMAT
0_7 | 5 | enabled | POC; 3 | POC; 6 | 1 | 1.034 | No | Both | DMAT

## Balanced Fault
Test | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Type | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
1 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
2 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Both | DMAT
3 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Both | DMAT
4 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Both | DMAT
5 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | Both | DMAT
6 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Both | DMAT
7 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Both | DMAT
8 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
9 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
10 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Both | DMAT
11 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
12 | 10 | 5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
13 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | Both | DMAT
14 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Both | DMAT
15 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Both | DMAT
16 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Both | DMAT
17 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Both | DMAT
18 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Both | DMAT
19 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Both | DMAT
20 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
21 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
22 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Both | DMAT
23 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
24 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
25 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | 0 | No | Both | DMAT
26 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | -0.3 | No | Both | DMAT
27 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 1 | 0.3 | No | Both | DMAT
28 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 14 | 1 | 0 | No | Both | DMAT
29 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 1 | -0.3 | No | Both | DMAT
30 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 1 | 0.3 | No | Both | DMAT
31 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | 0 | No | Both | DMAT
32 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
33 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
34 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 14 | 0.05 | 0 | No | Both | DMAT
35 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
36 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT

## Unbalanced Fault
Test | Fault Duration (s) | End Run (s) | Apply Fault (s) | Fault Type | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | DMAT | PSCAD
37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
85-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
91-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 0.05 | 0 | No | Reduced_DMAT | PSCAD
92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | DMAT | PSCAD
98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD
109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | DMAT | PSCAD
109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | DMAT | PSCAD
110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | DMAT | PSCAD
111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | DMAT | PSCAD
112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | DMAT | PSCAD
113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | DMAT | PSCAD
114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | DMAT | PSCAD
115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | DMAT | PSCAD
115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | DMAT | PSCAD
116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | DMAT | PSCAD
117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | DMAT | PSCAD
118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | DMAT | PSCAD
119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | DMAT | PSCAD
120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | DMAT | PSCAD

## Temporary Over Voltage
Test | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | DMAT | PSCAD
132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | DMAT | PSCAD
133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | DMAT | PSCAD
134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | DMAT | PSCAD
135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | DMAT | PSCAD
136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | DMAT | PSCAD
137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
138 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | DMAT | PSCAD
139 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | DMAT | PSCAD
140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | DMAT | PSCAD
141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | DMAT | PSCAD
142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | DMAT | PSCAD
143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | DMAT | PSCAD
144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | DMAT | PSCAD
145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | DMAT | PSCAD
146 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
147 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | DMAT | PSCAD
148 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | DMAT | PSCAD

## MFRT
Test | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
121 | 60 | 5 | S1 | 0.25 | POC | POC | 1 | 0 | No | PSCAD | Reduced_DMAT
122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | No | PSCAD | Reduced_DMAT
123 | 60 | 5 | S3 | S3 | POC | POC | 1 | 0 | No | PSCAD | DMAT
124 | 60 | 5 | S4 | S4 | POC | POC | 1 | 0 | No | PSCAD | DMAT
125 | 60 | 5 | S5 | S5 | POC | POC | 1 | 0 | Yes | PSCAD | DMAT
126 | 60 | 5 | P1 | P1 | POC | POC | 1 | 0 | No | PSSE | Reduced_DMAT
127 | 60 | 5 | P2 | P2 | POC | POC | 1 | 0 | No | PSSE | Reduced_DMAT
128 | 60 | 5 | P3 | P3 | POC | POC | 1 | 0 | No | PSSE | DMAT
129 | 60 | 5 | P4 | P4 | POC | POC | 1 | 0 | No | PSSE | DMAT
130 | 60 | 5 | P5 | P5 | POC | POC | 1 | 0 | No | PSSE | DMAT

## Voltage Reference Step Change
Test | End Run (s) | Event | Time Steps (s) | Delta (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Suite | Software
149 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
150 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
151 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
152 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
153 | 45 | Vref | fig2 | fig2 | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
154 | 45 | Vref | fig2 | fig2 | POC | POC | 0.05 | 0 | Yes | DMAT | PSCAD
155 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
156 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
157 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
158 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
159 | 45 | Vgrid | fig3 | fig3 | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
160 | 45 | Vgrid | fig3 | fig3 | POC | POC | 0.05 | 0 | Yes | DMAT | PSCAD
161 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
162 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
163 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 1 | 0 | No | DMAT | PSCAD
164 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 0.05 | 0 | No | DMAT | PSCAD
165 | 45 | Qref | fig4 | fig4 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
166 | 45 | Qref | fig4 | fig4 | POC | POC | 0.05 | 0 | No | DMAT | PSCAD

## Active Power Reference Step
Test | End Run (s) | SCR | X/R | Time Steps (s) | Pref Deltas (pu) | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
167 | 35 | 10 | 14 | fig5 | fig5 | 1 | 0 | Yes | DMAT | PSCAD
168 | 35 | 3 | 14 | fig5 | fig5 | 1 | 0 | Yes | DMAT | PSCAD
169 | 35 | POC | POC | fig5 | fig5 | 1 | 0 | Yes | Reduced_DMAT | PSCAD

## Grid Frequency
Test | End Run (s) | Time Steps (s) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
170 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
171 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
172 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
173 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.05 | 0 | No | Both | Reduced_DMAT
174 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
175 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
176 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0 | No | Both | Reduced_DMAT
177 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.05 | 0 | No | Both | Reduced_DMAT

## Grid Voltage Change
Test | End Run (s) | Time Steps (s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Suite
178 | 65 | fig8 | fig8 | fig8 | 10 | 14; 3 | 1 | 0 | Yes | Both | DMAT
179 | 65 | fig8 | fig8 | fig8 | 3 | 14; 3 | 1 | 0 | Yes | Both | DMAT
180 | 65 | fig8 | fig8 | fig8 | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
181 | 65 | fig8 | fig8 | fig8 | POC | POC | 0.5 | 0 | Yes | Both | Reduced_DMAT
182 | 45 | fig9 | fig9 | fig9 | 10 | 14; 3 | 1 | 0 | Yes | Both | DMAT
183 | 45 | fig9 | fig9 | fig9 | 3 | 14; 3 | 1 | 0 | Yes | Both | DMAT
184 | 45 | fig9 | fig9 | fig9 | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
185 | 45 | fig9 | fig9 | fig9 | POC | POC | 0.5 | 0 | Yes | Both | Reduced_DMAT
186 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 10 | 14; 3 | 1 | 0 | Yes | Both | DMAT
187 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 3 | 14; 3 | 1 | 0 | Yes | Both | DMAT
188 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 1 | 0 | Yes | Both | Reduced_DMAT
189 | 12 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 0.5 | 0 | Yes | Both | Reduced_DMAT

## Grid Oscillation Rejection
Test | End Run (s) | Time Steps (s) | Osc Freqs (Hz) | Osc Magnitude (pu) | Step (Hz) | SCR | X/R | Osc Phase (deg) | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
190 | 20 | [5,15] | 0.1:0.9 | 0.005 | 0.1 | POC | POC | 0 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
191 | 20 | [5,15] | 1:45 | 0.005 | 1 | POC | POC | 0 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
192 | 20 | [5,15] | 0.1:0.9; 1:45 | 0.005 | 0.1; 1 | POC | POC | 2 | 1 | 0 | No | DMAT | PSCAD

## Grid Voltage Phase Angle Change
Test | End Run (s) | Apply Event (s) | Angle Change (deg) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
193 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
194 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
195 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 1 | 0 | Yes | DMAT | PSCAD
196 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
197 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
198 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 0.05 | 0 | Yes | DMAT | PSCAD

## SCR1 Active Power Ref Step
Test | Time Steps (s) | Pref Deltas (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | End Run (s) | Suite | Software
199 | fig12 | fig12 | 1 | 14; 3 | 0.05 | 0 | Yes | 30 | Reduced_DMAT | PSCAD

## SCR1 FRT
Test | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
200 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
201 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 0.5 | 0 | Yes | DMAT | PSCAD
202 | 8 | 5 | 0.43 | Zf=4xZs | [3,1] | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD
203 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 1 | 0 | Yes | Reduced_DMAT | PSCAD
204 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 0.5 | 0 | Yes | DMAT | PSCAD
205 | 8 | 5 | 0.43 | Zf=0 | [3,1] | 14; 3 | 0.05 | 0 | Yes | DMAT | PSCAD

## Site specific SCR FRT
Test | End Run (s) | Apply Fault (s) | Fault Duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Suite | Software
206 | 8 | 5 | 0.43 | Zf=0 | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
207 | 8 | 5 | 0.43 | Zf=0.11xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
208 | 8 | 5 | 0.43 | Zf=0.25xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
209 | 8 | 5 | 0.43 | Zf=0.42xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
210 | 8 | 5 | 0.43 | Zf=0.66xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
211 | 8 | 5 | 0.43 | Zf=1xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
212 | 8 | 5 | 0.43 | Zf=1.5xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
213 | 8 | 5 | 0.43 | Zf=2.3xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
214 | 8 | 5 | 0.43 | Zf=4xZs | POC | POC | 1 | 0 | No | Reduced_DMAT | PSCAD
215 | 8 | 5 | 0.43 | Zf=9xZs | POC | POC | 1 | 0 | Yes | Reduced_DMAT | PSCAD
216 | 8 | 5 | 0.43 | Zf=0 | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
217 | 8 | 5 | 0.43 | Zf=0.11xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
218 | 8 | 5 | 0.43 | Zf=0.25xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
219 | 8 | 5 | 0.43 | Zf=0.42xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
220 | 8 | 5 | 0.43 | Zf=0.66xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
221 | 8 | 5 | 0.43 | Zf=1xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
222 | 8 | 5 | 0.43 | Zf=1.5xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
223 | 8 | 5 | 0.43 | Zf=2.3xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
224 | 8 | 5 | 0.43 | Zf=4xZs | POC | POC | 0.5 | 0 | No | Reduced_DMAT | PSCAD
225 | 8 | 5 | 0.43 | Zf=9xZs | POC | POC | 0.5 | 0 | Yes | Reduced_DMAT | PSCAD

## CSR_S5251
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Voltage POC (pu) | Reactive Power (pu) | Time Steps (s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Action | Software | Suite
csr_s5251_1 | 20 | POC | POC | 1 | 0 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_2 | 20 | POC | POC | 1 | 0 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_3 | 20 | POC | POC | 1 | 0 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_4 | 20 | POC | POC | 1 | 0 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_5 | 20 | POC | POC | 1 | 0 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_6 | 20 | POC | POC | 1 | 0 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_7 | 20 | POC | POC | 1 | -1 | 0.9 | -1 |  |  |  | No | Both | CSR
csr_s5251_8 | 20 | POC | POC | 1 | -1 | 0.9 | 0 |  |  |  | No | Both | CSR
csr_s5251_9 | 20 | POC | POC | 1 | -1 | 0.9 | 1 |  |  |  | No | Both | CSR
csr_s5251_10 | 20 | POC | POC | 1 | -1 | 1.1 | -1 |  |  |  | No | Both | CSR
csr_s5251_11 | 20 | POC | POC | 1 | -1 | 1.1 | 0 |  |  |  | No | Both | CSR
csr_s5251_12 | 20 | POC | POC | 1 | -1 | 1.1 | 1 |  |  |  | No | Both | CSR
csr_s5251_13 | 20 | POC | POC | 0.53333 | 1 | 0.9 | -1 |  |  |  | No | Both | CSR
csr_s5251_14 | 20 | POC | POC | 0.53333 | 1 | 0.9 | 0 |  |  |  | No | Both | CSR
csr_s5251_15 | 20 | POC | POC | 0.53333 | 1 | 0.9 | 1 |  |  |  | No | Both | CSR
csr_s5251_16 | 20 | POC | POC | 0.53333 | 1 | 1.1 | -1 |  |  |  | No | Both | CSR
csr_s5251_17 | 20 | POC | POC | 0.53333 | 1 | 1.1 | 0 |  |  |  | No | Both | CSR
csr_s5251_18 | 20 | POC | POC | 0.53333 | 1 | 1.1 | 1 |  |  |  | No | Both | CSR
csr_s5251_19 | 20 | POC | POC | 0 | 1 | 0.9 | -1 |  |  |  | No | Both | CSR
csr_s5251_20 | 20 | POC | POC | 0 | 1 | 0.9 | 0 |  |  |  | No | Both | CSR
csr_s5251_21 | 20 | POC | POC | 0 | 1 | 0.9 | 1 |  |  |  | No | Both | CSR
csr_s5251_22 | 20 | POC | POC | 0 | 1 | 1.1 | -1 |  |  |  | No | Both | CSR
csr_s5251_23 | 20 | POC | POC | 0 | 1 | 1.1 | 0 |  |  |  | No | Both | CSR
csr_s5251_24 | 20 | POC | POC | 0 | 1 | 1.1 | 1 |  |  |  | No | Both | CSR
csr_s5251_25 | 20 | POC | POC | 0 | -1 | 0.9 | -1 |  |  |  | No | Both | CSR
csr_s5251_26 | 20 | POC | POC | 0 | -1 | 0.9 | 0 |  |  |  | No | Both | CSR
csr_s5251_27 | 20 | POC | POC | 0 | -1 | 0.9 | 1 |  |  |  | No | Both | CSR
csr_s5251_28 | 20 | POC | POC | 0 | -1 | 1.1 | -1 |  |  |  | No | Both | CSR
csr_s5251_29 | 20 | POC | POC | 0 | -1 | 1.1 | 0 |  |  |  | No | Both | CSR
csr_s5251_30 | 20 | POC | POC | 0 | -1 | 1.1 | 1 |  |  |  | No | Both | CSR
csr_s5251_31 | 20 | inf | inf | 1 | 0 | 1.034 | -1 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | Yes | Both | CSR
csr_s5251_32 | 20 | inf | inf | 0 | -1 | 1.034 | -1 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | Yes | Both | CSR
csr_s5251_33 | 22 | inf | inf | 1 | 0 | 1.034 | 1 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | Yes | Both | CSR
csr_s5251_34 | 22 | inf | inf | 0 | -1 | 1.034 | 1 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | Yes | Both | CSR

## CSR_S5253
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Voltage POC (pu) | Reactive Power (pu) | Time Steps (s) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Action | Software | Suite
csr_s5253_1 | 15 | inf | inf | 1 | 0 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_2 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_3 | 15 | inf | inf | 1 | 0 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_4 | 15 | inf | inf | 1 | -1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_5 | 15 | inf | inf | 1 | -1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_6 | 15 | inf | inf | 1 | -1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_7 | 15 | inf | inf | 0.53333 | 1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_8 | 15 | inf | inf | 0.53333 | 1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_9 | 15 | inf | inf | 0.53333 | 1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_10 | 15 | inf | inf | 0 | 1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_11 | 15 | inf | inf | 0 | 1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_12 | 15 | inf | inf | 0 | 1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_13 | 15 | inf | inf | 0 | -1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_14 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_15 | 15 | inf | inf | 0 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_16 | 15 | inf | inf | 1 | 0 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_17 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_18 | 15 | inf | inf | 1 | 0 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_19 | 15 | inf | inf | 1 | -1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_20 | 15 | inf | inf | 1 | -1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_21 | 15 | inf | inf | 1 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_22 | 15 | inf | inf | 0.53333 | 1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_23 | 15 | inf | inf | 0.53333 | 1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_24 | 15 | inf | inf | 0.53333 | 1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_25 | 15 | inf | inf | 0 | 1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_26 | 15 | inf | inf | 0 | 1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_27 | 15 | inf | inf | 0 | 1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_28 | 15 | inf | inf | 0 | -1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_29 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_30 | 120 | inf | inf | 0 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | No | PSCAD | CSR
csr_s5253_31 | 120 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,120] | [0,-1,-3,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_32 | 120 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.5833,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_33 | 600 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.25,3.5833,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_34 | 1200 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,1200] | [0,-1,0,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_35 | 1200 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.125,3.9167,120] | [0,-0.5,0,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_36 | 1200 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.125,3.9167,120] | [0,0.5,0,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_37 | 600 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,120] | [0,1,0,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_38 | 120 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.9167,120] | [0,1,3,0,0] | [false,true,true,false,false] | No | PSSE | CSR
csr_s5253_39 | 600 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.25,3.9167,120] | [0,1,3,0,0] | [false,true,true,false,false] | No | PSSE | CSR

## CSR_S5254
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Voltage POC (pu) | Reactive Power (pu) | Time Steps (s) | Vgrid Deltas (pu) | Vgrid Ramp (Hz/s) | Action | Software | Suite
csr_s5254_1 | 10 | inf | inf | 1 | 0 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_2 | 10 | inf | inf | 1 | 0 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_3 | 10 | inf | inf | 1 | 0 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_4 | 10 | inf | inf | 1 | -1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_5 | 10 | inf | inf | 1 | -1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_6 | 10 | inf | inf | 1 | -1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_7 | 10 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_8 | 10 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_9 | 10 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | Yes | PSCAD | CSR
csr_s5254_10 | 10 | inf | inf | 0 | 1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_11 | 10 | inf | inf | 0 | 1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_12 | 10 | inf | inf | 0 | 1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_13 | 10 | inf | inf | 0 | -1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_14 | 10 | inf | inf | 0 | -1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_15 | 10 | inf | inf | 0 | -1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_16 | 15 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_17 | 15 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_18 | 15 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_19 | 15 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_20 | 15 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_21 | 15 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_22 | 15 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_23 | 15 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_24 | 15 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_25 | 15 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_26 | 15 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_27 | 15 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_28 | 15 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_29 | 15 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_30 | 15 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_31 | 10 | inf | inf | 1 | 0 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_32 | 10 | inf | inf | 1 | 0 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_33 | 10 | inf | inf | 1 | 0 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_34 | 10 | inf | inf | 1 | -1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_35 | 10 | inf | inf | 1 | -1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_36 | 10 | inf | inf | 1 | -1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_37 | 10 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_38 | 10 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_39 | 10 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_40 | 10 | inf | inf | 0 | 1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_41 | 10 | inf | inf | 0 | 1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_42 | 10 | inf | inf | 0 | 1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_43 | 10 | inf | inf | 0 | -1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_44 | 10 | inf | inf | 0 | -1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_45 | 10 | inf | inf | 0 | -1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_46 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_47 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_48 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_49 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_50 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_51 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_52 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_53 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_54 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_55 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_56 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_57 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_58 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_59 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_60 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | No | PSCAD | CSR

## CSR_S5255
Test | End Run (s) | Apply Fault (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Reactive Power (pu) | Fault Duration (s) | Fault Type | Applied Fault Voltage (pu) | Voltage Step (pu) | Fault X/R | Action | Software | Reduced DMAT
csr_s5255_1 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_2 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_3 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_4 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_5 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_6 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_7 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_8 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_9 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_10 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_11 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_12 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_13 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_14 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_15 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_16 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_17 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_18 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_19 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_20 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_21 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_22 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_23 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_24 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_25 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_26 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_27 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_28 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_29 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_30 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_31 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_32 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_33 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_34 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_35 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_36 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_37 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_38 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_39 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_40 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_41 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_42 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_43 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_44 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_45 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_46 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_47 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_48 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT

## CSR_S52511
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Reactive Power (pu) | Time Steps (s) | Freq Deltas (Hz) | Freq Ramp (Hz/s) | Action | Software | Suite
csr_s5253_1 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_2 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_3 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_4 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_5 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_6 | 16 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_7 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_8 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_9 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_10 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_11 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_12 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-1,-1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_13 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_14 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_15 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_16 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_17 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_18 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-0.05,-0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_19 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_20 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_21 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_22 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_23 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_24 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,-0.015,-0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_25 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_26 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_27 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_28 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_29 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_30 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,0.015,0.015] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_31 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_32 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_33 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_34 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_35 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_36 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,0.05,0.05] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_37 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_38 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_39 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_40 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_41 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_42 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,1,1] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_43 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_44 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_45 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_46 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_47 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR
csr_s5253_48 | 16 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0,2,2] | [false,true,false,false] | No | PSCAD | CSR

## CSR_S52513
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Reactive Power (pu) | Time Steps (s) | Vgrid Deltas (pu) | Vref Deltas (pu) | Action | Software | Suite
csr_s52513_1 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_2 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_3 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_4 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_5 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_6 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_7 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_8 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_9 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_10 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_11 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_12 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_13 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_14 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | No | Both | CSR
csr_s52513_15 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_16 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_17 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_18 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_19 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_20 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_21 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_22 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_23 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_24 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_25 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_26 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_27 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_28 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_29 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_30 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | No | Both | CSR
csr_s52513_31 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_32 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_33 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_34 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_35 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_36 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.05,-0.1, 0.00] |  | No | Both | CSR
csr_s52513_37 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_38 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_39 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_40 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_41 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_42 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.1,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_43 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_44 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_45 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_46 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_47 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_48 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_49 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_50 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_51 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_52 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_53 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_54 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_55 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_56 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | No | Both | CSR
csr_s52513_57 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_58 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_59 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_60 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_61 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_62 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_63 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_64 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_65 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_66 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_67 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_68 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_69 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_70 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | No | Both | CSR
csr_s52513_71 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_72 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_73 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_74 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_75 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_76 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_77 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_78 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_79 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_80 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_81 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_82 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_83 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_84 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | No | Both | CSR
csr_s52513_85 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_86 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_87 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_88 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_89 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_90 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_91 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_92 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_93 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_94 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_95 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_96 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_97 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_98 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_99 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_100 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | No | Both | CSR
csr_s52513_101 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_102 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_103 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_104 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_105 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_106 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_107 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_108 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_109 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_110 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_111 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_112 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1, 0.00] | No | Both | CSR
csr_s52513_113 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_114 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_115 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_116 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_117 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_118 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_119 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_120 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_121 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_122 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_123 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_124 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_125 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_126 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | No | Both | CSR
csr_s52513_127 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_128 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_129 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_130 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_131 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_132 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_133 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_134 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_135 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_136 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_137 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_138 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_139 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR
csr_s52513_140 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | No | Both | CSR

## CSR_S52514
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Reactive Power (pu) | Time Steps (s) | WTG Pref Deltas (pu) | WTG Pref Ramp (pu/s) | BESS Pref Deltas (pu) | BESS Pref Ramp (pu/s) | Action | Software | Suite
csr_s52514_1 | 180 | POC | POC | 1 | 0 | 1.034 | -1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | Yes | Both | CSR
csr_s52514_2 | 180 | POC | POC | 1 | 0 | 1.034 | 0 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | Yes | Both | CSR
csr_s52514_3 | 180 | POC | POC | 1 | 0 | 1.034 | 1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | Yes | Both | CSR
csr_s52514_4 | 180 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_5 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_6 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_7 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_8 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_9 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_10 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_11 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_12 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_13 | 180 | POC | POC | 0 | -1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_14 | 180 | POC | POC | 0 | -1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_15 | 180 | POC | POC | 0 | -1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,0.5,0.5,0.5] | [false,false,false,false] | No | Both | CSR
csr_s52514_16 | 180 | POC | POC | 1 | 0 | 1.034 | -1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_17 | 180 | POC | POC | 1 | 0 | 1.034 | 0 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_18 | 180 | POC | POC | 1 | 0 | 1.034 | 1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_19 | 180 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_20 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_21 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] |  |  | No | Both | CSR
csr_s52514_22 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_23 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_24 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_25 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_26 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_27 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_28 | 180 | POC | POC | 0 | -1 | 1.034 | -1 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_29 | 180 | POC | POC | 0 | -1 | 1.034 | 0 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR
csr_s52514_30 | 180 | POC | POC | 0 | -1 | 1.034 | 1 | [0,5,65,125] |  |  | [0,0.95,0.95,0.95] | [false,false,false,false] | No | Both | CSR

## CSR_S52516
Test | End Run (s) | Apply Event (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Reactive Power (pu) | Angle Change (deg) | Action | Software | Suite
csr_s52516_1 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_2 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_3 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_4 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_5 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_6 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_7 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_8 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_9 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_10 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | -1 | 20 | No | Both | CSR
csr_s52516_11 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 0 | 20 | No | Both | CSR
csr_s52516_12 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 1 | 20 | No | Both | CSR
csr_s52516_13 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 20 | No | Both | CSR
csr_s52516_14 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 20 | No | Both | CSR
csr_s52516_15 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 20 | No | Both | CSR
csr_s52516_16 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | -20 | No | Both | CSR
csr_s52516_17 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | -20 | No | Both | CSR
csr_s52516_18 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | -20 | No | Both | CSR
csr_s52516_19 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | -1 | -20 | No | Both | CSR
csr_s52516_20 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 0 | -20 | No | Both | CSR
csr_s52516_21 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 1 | -20 | No | Both | CSR
csr_s52516_22 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | -1 | -20 | No | Both | CSR
csr_s52516_23 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 0 | -20 | No | Both | CSR
csr_s52516_24 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 1 | -20 | No | Both | CSR
csr_s52516_25 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | -1 | -20 | No | Both | CSR
csr_s52516_26 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 0 | -20 | No | Both | CSR
csr_s52516_27 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 1 | -20 | No | Both | CSR
csr_s52516_28 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | -20 | No | Both | CSR
csr_s52516_29 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | -20 | No | Both | CSR
csr_s52516_30 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | -20 | No | Both | CSR