## System_inf
Var name | Var Val | unit
Workspacename
CaseName
POC Bus Name | 101
Terminal Bus Name | 102
V_POC | 1.034 | pu
Nominal Power | 150 | MW
Plant Capacity | 150 | MVA
Fault level | 901.186 | MVA
POC SCR | [12.676303,2.2863071]
POC XR ratio | [6.66,5.33]
POC base Voltage | 220 | kV
Nominal Frequency | 50 | Hz
Qlead,Qlag | [0.3,-0.3]
Save Format | csv | out,csv
Time step | 16.6667 | us
Channel plot | 200 | us
Q-V Droop | 0.05
Suite | Reduced_DMAT

## PPC_Signals
Signals | Variable | Value
PPC name
Pref
Qref | Qcm
PFref | PFref
Vdroop | Vref
id
iq
Inverter Name
Q_control_mode | Droop
Is Inside module activated? | No
Module Name

## V_droop
Qmax | Qmin | Qnom | P-slope | N-slope | deadband1 | deadband2 | deadband |  | Qbase-Vestas(MW) | Vref | Qoffset | Vmax
118.5 | -118.5 | 0 | 39.5 | 39.5 | 1 | 1 | 0 | 0.04 | 1.975 | 1 | 0 | 1.05

## ReadMe
WIP
For any steps, the delta values are the final values measured from the initial value
ramp rates are not used, adjust the time and delta values to modify ramp rates

## Checklist
Checklist | Action
Flat Run | Yes
Snapshot | Yes
Balanced Fault | Yes
Unbalanced Fault | Yes
MFRT | Yes
Temporary Over Voltage | Yes
Voltage Reference Step Change | Yes
Active Power Reference Step | Yes
Grid Frequency | Yes
Grid Voltage Change | Yes
Grid Oscillation Rejection | Yes
Grid Voltage Phase Angle Change | Yes
SCR1 Active Power Ref Step | Yes
SCR1 FRT | Yes
Site specific SCR FRT | Yes
CSR_S5251 | No
CSR_S5253 | No
CSR_S5254 | No
CSR_S5255 | No
CSR_S52511 | No
CSR_S52512 | No
CSR_S52513 | No
CSR_S52514 | No
CSR_S52516 | No

## Snapshot
Test | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Reduced DMAT | Suite
0.4 | 5 | 3 | 10 | 6 | 1 | Yes | Yes | Reduced_DMAT
0.5 | 5 | 3 | 3 | 6 | 1 | Yes | No

## Flat Run
Test | End Run (s) | Time Steps (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | WTG Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
0.1 | 301 |  | enabled | POC; 5 | POC; 6 | 1 |  |  | 1.034 | 0 | Yes | Both | Reduced_DMAT
0.2 | 301 |  | disabled | POC; 5 | POC; 6 | 1 |  |  | 1.034 | 0 | No | PSCAD | Reduced_DMAT
0.3 | 301 |  | enabled | POC; 5 | POC; 6 | 0.05 |  |  | 1.034 | 0 | Yes | Both | Reduced_DMAT
0.4 | 5 |  | enabled | POC; 10 | POC; 6 | 1 |  |  | 1.034 | 0 | No | Both | Reduced_DMAT
0.5 | 5 |  | enabled | POC; 3 | POC; 6 | 1 |  |  | 1.034 | 0 | No | Both | DMAT

## Unbalanced Fault
Test | Fault duration (s) | End Run (s) | Apply fault (s) | Fault type | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Action2 | Reduced DMAT | Suite
37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | No | Yes | No
37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | Reduced_DMAT
38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No
39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No
40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No
41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | Yes | No
42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No
43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No
43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | Reduced_DMAT
44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No
45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No
46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No
47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No
48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No
49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | Yes | No
49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes | Yes | Reduced_DMAT
50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Yes | No
51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Yes | No
52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Yes | No
53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Yes | No
54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Yes | No
55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Yes | No
55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes | Yes | Reduced_DMAT
56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Yes | No
57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Yes | No
58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Yes | No
59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Yes | No
60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Yes | No
61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | Yes | No
61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | Reduced_DMAT
62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No
63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No
64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No
65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | Yes | Yes | No
66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No
67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No
67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | Reduced_DMAT
68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No
69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No
70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No
71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No
72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No
73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | Yes | No
73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes | Yes | Reduced_DMAT
74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | Yes | No
75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | Yes | No
76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | Yes | No
77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | Yes | No
78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | Yes | No
79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | Yes | No
79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes | Yes | Reduced_DMAT
80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | Yes | No
81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | Yes | No
82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | Yes | No
83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | Yes | No
84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | Yes | No
85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | Yes | No
85-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 1 | 0 | No | Yes | Yes | Reduced_DMAT
86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | Yes | No
87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | Yes | No
88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | Yes | No
89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | Yes | No
90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | Yes | No
91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | Yes | No
91-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 0.05 | 0 | No | Yes | Yes | Reduced_DMAT
92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | Yes | No
93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | Yes | No
94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | Yes | No
95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | Yes | No
96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | Yes | No
97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | Yes | No
97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | Yes | No
98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | Yes | No
99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | Yes | No
100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | Yes | No
101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | Yes | No
102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | Yes | No
103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | Yes | No
103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | Yes | No
104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | Yes | No
105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | Yes | No
106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | Yes | No
107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | Yes | No
108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | Yes | No
109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | Yes | No
109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | Yes | No
110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | Yes | No
111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | Yes | No
112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | Yes | No
113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | Yes | Yes | No
114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | Yes | No
115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | Yes | No
115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | Yes | No
116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | Yes | No
117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | Yes | No
118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | Yes | No
119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | Yes | No
120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | Yes | No

## Balanced Fault
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault type | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Reduced DMAT | Suite
1 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
2 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | -0.3 | No | Both | DMAT
3 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0.3 | No | Both | DMAT
4 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 1 | 0 | No | Both | DMAT
5 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | -0.3 | No | Both | DMAT
6 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | 0.3 | Yes | Both | DMAT
7 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0 | No | Both | DMAT
8 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
9 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
10 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 0.05 | 0 | No | Both | DMAT
11 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
12 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
13 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0 | No | Both | DMAT
14 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | -0.3 | No | Both | DMAT
15 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0.3 | No | Both | DMAT
16 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 1 | 0 | No | Both | DMAT
17 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | -0.3 | No | Both | DMAT
18 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | 0.3 | No | Both | DMAT
19 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0 | No | Both | DMAT
20 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
21 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
22 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 0.05 | 0 | No | Both | DMAT
23 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
24 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT
25 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0 | No | Both | DMAT
26 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | -0.3 | No | Both | DMAT
27 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0.3 | No | Both | DMAT
28 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 1 | 0 | No | Both | DMAT
29 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | -0.3 | No | Both | DMAT
30 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | 0.3 | No | Both | DMAT
31 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0 | No | Both | DMAT
32 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | -0.3 | No | Both | DMAT
33 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0.3 | No | Both | DMAT
34 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 0.05 | 0 | No | Both | DMAT
35 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | -0.3 | No | Both | DMAT
36 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | 0.3 | No | Both | DMAT

## Temporary Over Voltage
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | No
132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | No
133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | No
134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | No
135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | No
136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | No
137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Yes | Reduced_DMAT
138 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | No
139 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | No
140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | No
141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | No
142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | No
143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | No
144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | No
145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | No
146 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Yes | Reduced_DMAT
147 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | No
148 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | No

## MFRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Software | Suite
121 | 60 | 5 | S1 | 0.25 | POC | POC | 1 | 0 | No | Yes | PSCAD | Reduced_DMAT
122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | No | Yes | PSCAD | Reduced_DMAT
123 | 60 | 5 | S3 | S3 | POC | POC | 1 | 0 | No | No | PSCAD
124 | 60 | 5 | S4 | S4 | POC | POC | 1 | 0 | No | No | PSCAD
125 | 60 | 5 | S5 | S5 | POC | POC | 1 | 0 | Yes | No | PSCAD
126 | 60 | 5 | P1 | P1 | POC | POC | 1 | 0 | No | Yes | PSSE
127 | 60 | 5 | P2 | P2 | POC | POC | 1 | 0 | No | Yes | PSSE
128 | 60 | 5 | P3 | P3 | POC | POC | 1 | 0 | No | No | PSSE
129 | 60 | 5 | P4 | P4 | POC | POC | 1 | 0 | No | No | PSSE
130 | 60 | 5 | P5 | P5 | POC | POC | 1 | 0 | No | No | PSSE

## Voltage Reference Step Change
Test | End Run (s) | Event | Time Steps (s) | Delta (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT | Suite
149 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 1 | 0 | Yes | No
150 | 45 | Vref | fig2 | fig2 | 10 | 14; 3 | 0.05 | 0 | Yes | No
151 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 1 | 0 | Yes | No
152 | 45 | Vref | fig2 | fig2 | 3 | 14; 3 | 0.05 | 0 | Yes | No
153 | 45 | Vref | fig2 | fig2 | POC | POC | 1 | 0 | Yes | Yes | Reduced_DMAT
154 | 45 | Vref | fig2 | fig2 | POC | POC | 0.05 | 0 | Yes | No
155 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 1 | 0 | Yes | No
156 | 45 | Vgrid | fig3 | fig3 | 10 | 14; 3 | 0.05 | 0 | Yes | No
157 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 1 | 0 | Yes | No
158 | 45 | Vgrid | fig3 | fig3 | 3 | 14; 3 | 0.05 | 0 | Yes | No
159 | 45 | Vgrid | fig3 | fig3 | POC | POC | 1 | 0 | Yes | Yes | Reduced_DMAT
160 | 45 | Vgrid | fig3 | fig3 | POC | POC | 0.05 | 0 | Yes | No
161 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 1 | 0 | Yes | No
162 | 45 | Qref | fig4 | fig4 | 10 | 14; 3 | 0.05 | 0 | Yes | No
163 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 1 | 0 | Yes | No
164 | 45 | Qref | fig4 | fig4 | 3 | 14; 3 | 0.05 | 0 | Yes | No
165 | 45 | Qref | fig4 | fig4 | POC | POC | 1 | 0 | Yes | Yes
166 | 45 | Qref | fig4 | fig4 | POC | POC | 0.05 | 0 | Yes | No

## Active Power Reference Step
Test | End Run (s) | SCR | X/R | Time Steps (s) | Pref_deltas (pu) | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
167 | 35 | 10 | 14 | fig5 | fig5 | 1 | 0 | Yes | No
168 | 35 | 3 | 14 | fig5 | fig5 | 1 | 0 | Yes | No
169 | 35 | POC | POC | fig5 | fig5 | 1 | 0 | Yes | Yes | Reduced_DMAT

## Grid Frequency
Test | End Run (s) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | SCR | X/R | Available Power (%) | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
170 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
171 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
172 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
173 | 25 | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | fig6_52-fast; fig6_51p75-fast; fig6_51p5-fast; fig6_52-slow | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
174 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
175 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
176 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
177 | 25 | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | fig7_47-fast; fig7_47-slow | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT

## Grid Voltage Change
Test | End Run (s) | Time Steps (s) | Vpoc_delta (pu) | Vpoc ramp (Hz/s) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Software | Suite
178 | 65 | fig8 | fig8 | fig8 | 10 | 14; 3 | 1 | 0 | Both | DMAT
179 | 65 | fig8 | fig8 | fig8 | 3 | 14; 3 | 1 | 0 | Both | DMAT
180 | 65 | fig8 | fig8 | fig8 | POC | POC | 1 | 0 | Both | Reduced_DMAT
181 | 65 | fig8 | fig8 | fig8 | POC | POC | 0.5 | 0 | Both | Reduced_DMAT
182 | 45 | fig9 | fig9 | fig9 | 10 | 14; 3 | 1 | 0 | Both | DMAT
183 | 65 | fig9 | fig9 | fig9 | 3 | 14; 3 | 1 | 0 | Both | DMAT
184 | 65 | fig9 | fig9 | fig9 | POC | POC | 1 | 0 | Both | Reduced_DMAT
185 | 65 | fig9 | fig9 | fig9 | POC | POC | 0.5 | 0 | Both | Reduced_DMAT
186 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 10 | 14; 3 | 1 | 0 | Both | DMAT
187 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | 3 | 14; 3 | 1 | 0 | Both | DMAT
188 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 1 | 0 | Both | Reduced_DMAT
189 | 65 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | fig10_dip10; fig10_dip50; fig10_dip80 | POC | POC | 0.5 | 0 | Both | Reduced_DMAT

## Grid Oscillation Rejection
Test | End Run (s) | Time Steps (s) | Osc_freq | Magnitude | Step (Hz) | SCR | X/R | Osc_Phase_deg | Active Power (pu) | Reactive Power | Action | Reduced DMAT | Suite
190 | 20 | [5,15] | 0.1:0.9 | 0.005 | 0.1 | POC | POC | 0 | 1 | 0 | Yes | Yes | Reduced_DMAT
191 | 20 | [5,15] | 1:45 | 0.005 | 1 | POC | POC | 0 | 1 | 0 | Yes | Yes | Reduced_DMAT
192 | 20 | [5,15] | 0.1:0.9; 1:45 | 0.005 | 0.1; 1 | POC | POC | 2 | 1 | 0 | No | No

## Grid Voltage Phase Angle Change
Test | End Run (s) | Apply event (s) | Angle Change | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Suite
193 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 1 | 0 | Yes | No
194 | 35 | 5 | 40; -40; 60; -60 | 10 | 14; 3 | 0.05 | 0 | Yes | No
195 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 1 | 0 | Yes | No
196 | 35 | 5 | 40; -40; 60; -60 | 3 | 14; 3 | 0.05 | 0 | Yes | No
197 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 1 | 0 | Yes | Yes | Reduced_DMAT
198 | 35 | 5 | 40; -40; 60; -60 | POC | POC | 0.05 | 0 | Yes | No

## SCR1 Active Power Ref Step
Test | Time Steps (s) | Pref_deltas (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT | End Run (s) | Suite
199 | fig12 | fig12 | 1 | 14; 3 | 0.05 | 0 | Yes | Yes | 35 | Reduced_DMAT

## SCR1 FRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Reduced DMAT | Suite
200 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6 | Yes | Reduced_DMAT
201 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 0.5 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6 | No
202 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | [3,1] | 14; 3 | 0.05 | 0 | Yes | 2.0058 | [1.05,1.05] | 4 | 6 | No
203 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 1 | 0 | Yes | 3.0058 | [1.05,1.05] | 4 | 6 | Yes | Reduced_DMAT
204 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 0.5 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6 | No
205 | 8 | 5 | 0.43 | Zf=0 | 0 | [3,1] | 14; 3 | 0.05 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6 | No

## Site specific SCR FRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Retain voltage method | Tx_Tap | Xmin | Xmax | Reduced DMAT | Suite
206 | 8 | 5 | 0.43 | Zf=0 | ~0 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
207 | 8 | 5 | 0.43 | Zf=0.11xZs | ~0.1 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
208 | 8 | 5 | 0.43 | Zf=0.25xZs | ~0.2 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
209 | 8 | 5 | 0.43 | Zf=0.42xZs | ~0.3 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
210 | 8 | 5 | 0.43 | Zf=0.66xZs | ~0.4 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
211 | 8 | 5 | 0.43 | Zf=1xZs | ~0.5 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
212 | 8 | 5 | 0.43 | Zf=1.5xZs | ~0.6 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
213 | 8 | 5 | 0.43 | Zf=2.3xZs | ~0.7 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
214 | 8 | 5 | 0.43 | Zf=4xZs | ~0.8 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
215 | 8 | 5 | 0.43 | Zf=9xZs | ~0.9 | POC | POC | 1 | 0 | Yes | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
216 | 8 | 5 | 0.43 | Zf=0 | 0 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
217 | 8 | 5 | 0.43 | Zf=0.11xZs | ~0.1 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
218 | 8 | 5 | 0.43 | Zf=0.25xZs | ~0.2 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
219 | 8 | 5 | 0.43 | Zf=0.42xZs | ~0.3 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
220 | 8 | 5 | 0.43 | Zf=0.66xZs | ~0.4 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
221 | 8 | 5 | 0.43 | Zf=1xZs | ~0.5 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
222 | 8 | 5 | 0.43 | Zf=1.5xZs | ~0.6 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
223 | 8 | 5 | 0.43 | Zf=2.3xZs | ~0.7 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
224 | 8 | 5 | 0.43 | Zf=4xZs | ~0.8 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT
225 | 8 | 5 | 0.43 | Zf=9xZs | ~0.9 | POC | POC | 0.5 | 0 | Yes | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes | Reduced_DMAT

## Figure References
Suite | Type | Figure | Time_steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,0,-0.05,0,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.3,-0.3,0,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.95,0,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,0,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,2,2,0,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-30,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,-3,-3,0,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,-0.1,-0.1,0.1,0.1,-0.1,-0.1,0,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.1,0.1,0,0] | [false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.5,-0.2,-0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.5,12] | [0,-0.2,0,0] | [false,false,true,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1,1] | [false,false,false,false,false,false,false,false]

## CSR_S5251
Test | End Run (s) | SCR | X/R | WTG Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Time Steps (s) | Vpoc_delta (pu) | Ramp/Step | Action | Software | Suite
csr_s5251_1 | 20 | POC | POC | 1 | 0 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_2 | 20 | POC | POC | 1 | 0 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_3 | 20 | POC | POC | 1 | 0 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_4 | 20 | POC | POC | 1 | 0 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_5 | 20 | POC | POC | 1 | 0 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_6 | 20 | POC | POC | 1 | 0 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_7 | 20 | POC | POC | 1 | -1 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_8 | 20 | POC | POC | 1 | -1 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_9 | 20 | POC | POC | 1 | -1 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_10 | 20 | POC | POC | 1 | -1 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_11 | 20 | POC | POC | 1 | -1 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_12 | 20 | POC | POC | 1 | -1 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_13 | 20 | POC | POC | 0.53333 | 1 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_14 | 20 | POC | POC | 0.53333 | 1 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_15 | 20 | POC | POC | 0.53333 | 1 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_16 | 20 | POC | POC | 0.53333 | 1 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_17 | 20 | POC | POC | 0.53333 | 1 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_18 | 20 | POC | POC | 0.53333 | 1 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_19 | 20 | POC | POC | 0 | 1 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_20 | 20 | POC | POC | 0 | 1 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_21 | 20 | POC | POC | 0 | 1 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_22 | 20 | POC | POC | 0 | 1 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_23 | 20 | POC | POC | 0 | 1 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_24 | 20 | POC | POC | 0 | 1 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_25 | 20 | POC | POC | 0 | -1 | 0.9 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_26 | 20 | POC | POC | 0 | -1 | 0.9 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_27 | 20 | POC | POC | 0 | -1 | 0.9 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_28 | 20 | POC | POC | 0 | -1 | 1.1 | -1 |  |  |  | Yes | Both | CSR
csr_s5251_29 | 20 | POC | POC | 0 | -1 | 1.1 | 0 |  |  |  | Yes | Both | CSR
csr_s5251_30 | 20 | POC | POC | 0 | -1 | 1.1 | 1 |  |  |  | Yes | Both | CSR
csr_s5251_31 | 20 | inf | inf | 1 | 0 | 1.034 | -1 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | Yes | Both | CSR
csr_s5251_32 | 20 | inf | inf | 0 | -1 | 1.034 | -1 | [0,5,20] | [0,0.066,0.066] | [false,false,false] | Yes | Both | CSR
csr_s5251_33 | 22 | inf | inf | 1 | 0 | 1.034 | 1 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | Yes | Both | CSR
csr_s5251_34 | 22 | inf | inf | 0 | -1 | 1.034 | 1 | [0,5,20] | [0,-0.134,-0.134] | [false,false,false] | Yes | Both | CSR

## CSR_S5253
Test | End Run (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | Action | Software | Suite
csr_s5253_1 | 15 | inf | inf | 1 | 0 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_2 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_3 | 15 | inf | inf | 1 | 0 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_4 | 15 | inf | inf | 1 | -1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_5 | 15 | inf | inf | 1 | -1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_6 | 15 | inf | inf | 1 | -1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_7 | 15 | inf | inf | 0.53333 | 1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_8 | 15 | inf | inf | 0.53333 | 1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_9 | 15 | inf | inf | 0.53333 | 1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_10 | 15 | inf | inf | 0 | 1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_11 | 15 | inf | inf | 0 | 1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_12 | 15 | inf | inf | 0 | 1 | 1.084 | 1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_13 | 15 | inf | inf | 0 | -1 | 0.984 | -1 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_14 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.25,3.9167,15] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_15 | 15 | inf | inf | 0 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_16 | 15 | inf | inf | 1 | 0 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_17 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_18 | 15 | inf | inf | 1 | 0 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_19 | 15 | inf | inf | 1 | -1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_20 | 15 | inf | inf | 1 | -1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_21 | 15 | inf | inf | 1 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_22 | 15 | inf | inf | 0.53333 | 1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_23 | 15 | inf | inf | 0.53333 | 1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_24 | 15 | inf | inf | 0.53333 |  | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_25 | 15 | inf | inf | 0 | 1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_26 | 15 | inf | inf | 0 | 1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_27 | 15 | inf | inf | 0 | 1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_28 | 15 | inf | inf | 0 | -1 | 0.984 | -1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_29 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_30 | 120 | inf | inf | 0 | -1 | 1.084 | 1 | [0,3,3.25,3.5833,15] | [0,1,2,0,0] | [false,true,true,false,false] | Yes | PSCAD | CSR
csr_s5253_31 | 120 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,120] | [0,-1,-3,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_32 | 120 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.5833,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_33 | 600 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.25,3.5833,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_34 | 1200 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,1200] | [0,-1,0,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_35 | 1200 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.125,3.9167,120] | [0,-0.5,0,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_36 | 1200 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.125,3.9167,120] | [0,0.5,0,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_37 | 600 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.25,3.9167,120] | [0,1,0,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_38 | 120 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.25,3.9167,120] | [0,1,3,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR
csr_s5253_39 | 600 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.25,3.9167,120] | [0,1,3,0,0] | [false,true,true,false,false] | Yes | PSSE | CSR

## CSR_S5254
Test | End Run (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc(pu) | Qpoc (pu) | Time Steps (s) | Vpoc_delta (pu) | Ramp/Step | Software | Suite
csr_s5254_1 | 10 | inf | inf | 1 | 0 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_2 | 10 | inf | inf | 1 | 0 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_3 | 10 | inf | inf | 1 | 0 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_4 | 10 | inf | inf | 1 | -1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_5 | 10 | inf | inf | 1 | -1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_6 | 10 | inf | inf | 1 | -1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_7 | 10 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_8 | 10 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_9 | 10 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_10 | 10 | inf | inf | 0 | 1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_11 | 10 | inf | inf | 0 | 1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_12 | 10 | inf | inf | 0 | 1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_13 | 10 | inf | inf | 0 | -1 | 1 | -1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_14 | 10 | inf | inf | 0 | -1 | 1 | 0 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_15 | 10 | inf | inf | 0 | -1 | 1 | 1 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_16 | 15 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_17 | 15 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_18 | 15 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_19 | 15 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_20 | 15 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_21 | 15 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_22 | 15 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_23 | 15 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_24 | 15 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_25 | 15 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_26 | 15 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_27 | 15 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_28 | 15 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_29 | 15 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_30 | 15 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_31 | 10 | inf | inf | 1 | 0 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_32 | 10 | inf | inf | 1 | 0 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_33 | 10 | inf | inf | 1 | 0 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_34 | 10 | inf | inf | 1 | -1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_35 | 10 | inf | inf | 1 | -1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_36 | 10 | inf | inf | 1 | -1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_37 | 10 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_38 | 10 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_39 | 10 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_40 | 10 | inf | inf | 0 | 1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_41 | 10 | inf | inf | 0 | 1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_42 | 10 | inf | inf | 0 | 1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_43 | 10 | inf | inf | 0 | -1 | 1 | -1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_44 | 10 | inf | inf | 0 | -1 | 1 | 0 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_45 | 10 | inf | inf | 0 | -1 | 1 | 1 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_46 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_47 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_48 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_49 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_50 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_51 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_52 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_53 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_54 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_55 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_56 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_57 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_58 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_59 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_60 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,15,10] | [0,-0.1,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.2,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_61 | 60 | inf | inf | 1 | 0 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_62 | 60 | inf | inf | 1 | 0 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_63 | 60 | inf | inf | 1 | 0 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_64 | 60 | inf | inf | 1 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_65 | 60 | inf | inf | 1 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_66 | 60 | inf | inf | 1 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_67 | 60 | inf | inf | 0.53333 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_68 | 60 | inf | inf | 0.53333 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_69 | 60 | inf | inf | 0.53333 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_70 | 60 | inf | inf | 0 | 1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_71 | 60 | inf | inf | 0 | 1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_72 | 60 | inf | inf | 0 | 1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_73 | 60 | inf | inf | 0 | -1 | 1 | -1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_74 | 60 | inf | inf | 0 | -1 | 1 | 0 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR
csr_s5254_75 | 60 | inf | inf | 0 | -1 | 1 | 1 | [0,5,7,10] | [0,-0.3,0,0] | [false,false,false,false] | PSCAD | CSR

## CSR_S5255
Test | End Run (s) | Apply fault (s) | SCR | X/R | WTG Pref (pu) | BESS Pref (pu) | Vref (pu) | Qpoc (pu) | Fault duration (s) | Fault type | Applied Fault Voltage (pu) | Step_size | Fault_X_to_R | Action | Software | Reduced DMAT
csr_s5255_1 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_2 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_3 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_4 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_5 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_6 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_7 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_8 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_9 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_10 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_11 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_12 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 3PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_13 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_14 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_15 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_16 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_17 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_18 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_19 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_20 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_21 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_22 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_23 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_24 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 1PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_25 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_26 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_27 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_28 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_29 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_30 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_31 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_32 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_33 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_34 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_35 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_36 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | 2PHG | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_37 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_38 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_39 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_40 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_41 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | No | Both | DMAT
csr_s5255_42 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 |  | Yes | Both | DMAT
csr_s5255_43 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_44 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_45 | 10 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_46 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_47 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT
csr_s5255_48 | 10 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 0.43 | L-L | 0.0001:0.9 | 0.03 | 2 | No | Both | DMAT

## CSR_S52511
Test | End Run (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vref (pu) | Qpoc (pu) | Time Steps (s) | Freq_Deltas (Hz) | Step/Ramp | Action | Software | Suite
csr_s5253_1 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_2 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_3 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_4 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_5 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_6 | 16 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,-2,-2,-2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_7 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_8 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_9 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_10 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_11 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_12 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,-1,-1,-1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_13 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_14 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_15 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_16 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_17 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_18 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,-0.05,-0.05,-0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_19 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_20 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_21 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_22 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_23 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_24 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,-0.015,-0.015,-0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_25 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_26 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_27 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_28 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_29 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_30 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0.015,0.015,0.015] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_31 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_32 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_33 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_34 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_35 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_36 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,0.05,0.05,0.05] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_37 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_38 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_39 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_40 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_41 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_42 | 15 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,1,1,1] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_43 | 15 | inf | inf | 1 | 0 | 1.034 | -1 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_44 | 15 | inf | inf | 1 | 0 | 1.034 | 0 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_45 | 15 | inf | inf | 1 | 0 | 1.034 | 1 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_46 | 15 | inf | inf | 0 | -1 | 1.034 | -1 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_47 | 15 | inf | inf | 0 | -1 | 1.034 | 0 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR
csr_s5253_48 | 16 | inf | inf | 0 | -1 | 1.034 | 1 | [0,3,3.5,15] | [0,2,2,2] | [false,true,false,false] | Yes | PSCAD | CSR

## CSR_S52513
Test | End Run (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vref (pu) | Qpoc (pu) | Time Steps (s) | Vpoc_Delta (pu) | Vref_Delta (pu) | Action | Software | Suite
csr_s52513_1 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_2 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_3 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_4 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_5 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_6 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_7 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_8 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_9 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_10 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_11 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_12 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_13 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_14 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_15 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_16 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_17 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_18 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_19 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_20 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_21 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_22 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_23 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_24 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_25 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_26 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_27 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_28 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_29 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_30 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] | [0,0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_31 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_32 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_33 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_34 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_35 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_36 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.05,-0.1 0.00] |  | Yes | Both | CSR
csr_s52513_37 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_38 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_39 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_40 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_41 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_42 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] | [0,0.1,-0.05 0.00] |  | Yes | Both | CSR
csr_s52513_43 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_44 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_45 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_46 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_47 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_48 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_49 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_50 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_51 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_52 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_53 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_54 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_55 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_56 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.01, 0.00] |  | Yes | Both | CSR
csr_s52513_57 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_58 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_59 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_60 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_61 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_62 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_63 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_64 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_65 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_66 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_67 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_68 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_69 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_70 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] | [0,-0.05, 0.00] |  | Yes | Both | CSR
csr_s52513_71 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_72 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_73 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_74 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_75 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_76 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_77 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_78 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_79 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_80 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_81 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_82 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_83 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_84 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.05, 0.00] | Yes | Both | CSR
csr_s52513_85 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_86 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_87 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_88 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_89 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_90 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_91 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_92 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_93 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_94 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_95 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_96 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_97 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_98 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_99 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_100 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,0.01, 0.00] | Yes | Both | CSR
csr_s52513_101 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_102 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_103 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_104 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_105 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_106 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.05,-0.1 0.00] | Yes | Both | CSR
csr_s52513_107 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_108 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_109 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_110 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_111 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_112 | 15 | POC | POC | 0 | -1 | 1.034 | 1 | [0,0.5,10.5,15] |  | [0,0.1,-0.05 0.00] | Yes | Both | CSR
csr_s52513_113 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_114 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_115 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_116 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_117 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_118 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_119 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_120 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_121 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_122 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_123 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_124 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_125 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_126 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.01, 0.00] | Yes | Both | CSR
csr_s52513_127 | 15 | POC | POC | 1 | 0 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_128 | 15 | POC | POC | 1 | 0 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_129 | 15 | POC | POC | 1 | 0 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_130 | 15 | POC | POC | 1 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_131 | 15 | POC | POC | 1 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_132 | 15 | POC | POC | 1 | -1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_133 | 15 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_134 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_135 | 15 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_136 | 15 | POC | POC | 0 | 1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_137 | 15 | POC | POC | 0 | 1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_138 | 15 | POC | POC | 0 | 1 | 1.034 | 1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_139 | 15 | POC | POC | 0 | -1 | 1.034 | -1 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR
csr_s52513_140 | 15 | POC | POC | 0 | -1 | 1.034 | 0 | [0,0.5,15] |  | [0,-0.05, 0.00] | Yes | Both | CSR

## CSR_S52514
Test | End Run (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vref (pu) | Qpoc (pu) | Time Steps (s) | Pref_deltas (pu) | Ramp/Step | Action | Software | Suite
csr_s52514_1 | 180 | POC | POC | 1 | 0 | 1.034 | -1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_2 | 180 | POC | POC | 1 | 0 | 1.034 | 0 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_3 | 180 | POC | POC | 1 | 0 | 1.034 | 1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_4 | 180 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_5 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_6 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_7 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_8 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_9 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.5,-0.5,-0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_10 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_11 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_12 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_13 | 180 | POC | POC | 0 | -1 | 1.034 | -1 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_14 | 180 | POC | POC | 0 | -1 | 1.034 | 0 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_15 | 180 | POC | POC | 0 | -1 | 1.034 | 1 | [0,5,65,125] | [0,0.5,0.5,0.5] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_16 | 180 | POC | POC | 1 | 0 | 1.034 | -1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_17 | 180 | POC | POC | 1 | 0 | 1.034 | 0 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_18 | 180 | POC | POC | 1 | 0 | 1.034 | 1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_19 | 180 | POC | POC | 0.53333 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_20 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_21 | 180 | POC | POC | 0.53333 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_22 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_23 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_24 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] | [0,-0.95,-0.95,-0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_25 | 180 | POC | POC | 0 | 1 | 1.034 | -1 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_26 | 180 | POC | POC | 0 | 1 | 1.034 | 0 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_27 | 180 | POC | POC | 0 | 1 | 1.034 | 1 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_28 | 180 | POC | POC | 0 | -1 | 1.034 | -1 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_29 | 180 | POC | POC | 0 | -1 | 1.034 | 0 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR
csr_s52514_30 | 180 | POC | POC | 0 | -1 | 1.034 | 1 | [0,5,65,125] | [0,0.95,0.95,0.95] | [false,false,false,false] | Yes | Both | CSR

## CSR_S52516
Test | End Run (s) | Apply event (s) | SCR | X/R | WTG_Pref (pu) | BESS_Pref (pu) | Vref (pu) | Qpoc (pu) | Angle Change | Action | Software | Suite
csr_s52516_1 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_2 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_3 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_4 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_5 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_6 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_7 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_8 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_9 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_10 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_11 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_12 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_13 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | 20 | Yes | Both | CSR
csr_s52516_14 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | 20 | Yes | Both | CSR
csr_s52516_15 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | 20 | Yes | Both | CSR
csr_s52516_16 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | -1 | -20 | Yes | Both | CSR
csr_s52516_17 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 0 | -20 | Yes | Both | CSR
csr_s52516_18 | 35 | 5 | POC | POC | 1 | 0 | 1.034 | 1 | -20 | Yes | Both | CSR
csr_s52516_19 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | -1 | -20 | Yes | Both | CSR
csr_s52516_20 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 0 | -20 | Yes | Both | CSR
csr_s52516_21 | 35 | 5 | POC | POC | 1 | -1 | 1.034 | 1 | -20 | Yes | Both | CSR
csr_s52516_22 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | -1 | -20 | Yes | Both | CSR
csr_s52516_23 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 0 | -20 | Yes | Both | CSR
csr_s52516_24 | 35 | 5 | POC | POC | 0.53333 | 1 | 1.034 | 1 | -20 | Yes | Both | CSR
csr_s52516_25 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | -1 | -20 | Yes | Both | CSR
csr_s52516_26 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 0 | -20 | Yes | Both | CSR
csr_s52516_27 | 35 | 5 | POC | POC | 0 | 1 | 1.034 | 1 | -20 | Yes | Both | CSR
csr_s52516_28 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | -1 | -20 | Yes | Both | CSR
csr_s52516_29 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 0 | -20 | Yes | Both | CSR
csr_s52516_30 | 35 | 5 | POC | POC | 0 | -1 | 1.034 | 1 | -20 | Yes | Both | CSR