## System_inf
Var name | Var Val | unit
Workspacename
CaseName
POC Bus Name | 101
Terminal Bus Name | 102
V_POC | 1.034 | pu
Nominal Power | 150 | MW
Plant Capacity | 150 | MVA
Fault level | 901.186 | MVA
POC SCR | [12.676303,2.2863071]
POC XR ratio | [6.66,5.33]
POC base Voltage | 220 | kV
Nominal Frequency | 50 | Hz
Qlead,Qlag | [0.3,-0.3]
Save Format | csv | out,csv
Time step | 16.6667 | us
Channel plot | 200 | us

## PPC_Signals
Signals | Variable | Value
PPC name
Pref
Qref | Qcm
PFref | PFref
Vdroop | Vref
id
iq
Inverter Name
Q_control_mode | Droop
Is Inside module activated? | No
Module Name

## V_droop
Qmax | Qmin | Qnom | P-slope | N-slope | deadband1 | deadband2 | deadband |  | Qbase-Vestas(MW) | Vref | Qoffset | Vmax
118.5 | -118.5 | 0 | 39.5 | 39.5 | 1 | 1 | 0 | 0.04 | 1.975 | 1 | 0 | 1.05

## Checklist
Checklist | Action
Flat Run | No
Snapshot | No
Balanced Faults | No
Unbalanced Faults | Yes
MFRT | No
Temporary Over voltage | Yes
Voltage reference step change | No
Active Power reference | No
Grid Frequency | No
Grid voltage change – response | No
Grid Oscillation rejection test | No
Grid voltage phase angle change | No
SCR1 active power test | No
SCR1 FRT | No
Site specific FRT | No

## Flat Run
Test | End Run (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | Action | Vgrid | Tx_Tap | Xmin | Xmax | Reduced DMAT
0.1 | 301 | enabled | 5 | 6 | 1 | Yes | 1.0456 | [1.05,1.05] | 1 | 301 | Yes
0.2 | 301 | disabled | 5 | 6 | 1 | Yes | 1.0456 | [1.05,1.05] | 1 | 301 | Yes
0.3 | 301 | enabled | 5 | 6 | 0.05 | Yes | 1.0569 | [1.05,1.0375] | 1 | 301 | Yes
0.4 | 5 | enabled | 5 | 6 | 1 | Yes | 1.0456 | [1.05,1.05] | 3 | 5 | Yes
0.5 | 5 | enabled | 3 | 2.7 | 2 | Yes | 0.9983 | [1.05,1.05] | 3 | 5 | No

## Snapshot
Test | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Reduced DMAT
0.4 | 5 | 3 | 10 | 6 | 1 | Yes | Yes
0.5 | 5 | 3 | 3 | 6 | 1 | Yes | No
0.6 | 5 | 3 | POC | POC | 1 | Yes | Yes
0.7 | 5 | 3 | POC | 6 | 1 | Yes | No
0.8 | 5 | 3 | 3 | POC | 1 | Yes | No

## Balanced Faults
Test | Fault duration (s) | Fault type | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | End Run (s) | Apply fault (s)
1 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | No | 60 | 20
2 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | -0.3 | Yes | No | 60 | 20
3 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 1 | 0.3 | Yes | No | 60 | 20
4 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 1 | 0 | Yes | No | 60 | 20
5 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | -0.3 | Yes | No | 60 | 20
6 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 1 | 0.3 | Yes | No | 60 | 20
7 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | No | 60 | 20
8 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | Yes | No | 60 | 20
9 | 0.43 | 3PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | Yes | No | 60 | 20
10 | 0.43 | 3PHG | Zf=0 | 3 | 14 | 0.05 | 0 | Yes | No | 60 | 20
11 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | Yes | No | 60 | 20
12 | 0.43 | 3PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | Yes | No | 60 | 20
13 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | No | 60 | 20
14 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | Yes | No | 60 | 20
15 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | Yes | No | 60 | 20
16 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 1 | 0 | Yes | No | 60 | 20
17 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | Yes | No | 60 | 20
18 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | Yes | No | 60 | 20
19 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | Yes | No | 60 | 20
20 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | Yes | No | 60 | 20
21 | 0.43 | 3PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | Yes | No | 60 | 20
22 | 0.43 | 3PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | Yes | No | 60 | 20
23 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | Yes | No | 60 | 20
24 | 0.43 | 3PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | Yes | No | 60 | 20
25 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 1 | 0 | Yes | No | 60 | 20
26 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 1 | -0.3 | Yes | No | 60 | 20
27 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 1 | 0.3 | Yes | No | 60 | 20
28 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 14 | 1 | 0 | Yes | No | 60 | 20
29 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 3 | 1 | -0.3 | Yes | No | 60 | 20
30 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 3 | 1 | 0.3 | Yes | No | 60 | 20
31 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 0.05 | 0 | Yes | No | 60 | 20
32 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 0.05 | -0.3 | Yes | No | 60 | 20
33 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 10 | 14 | 0.05 | 0.3 | Yes | No | 60 | 20
34 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 14 | 0.05 | 0 | Yes | No | 60 | 20
35 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 3 | 0.05 | -0.3 | Yes | No | 60 | 20
36 | 0.5 | 3PHG | Zf=2xZs[Udip=~0.7pu] | 3 | 3 | 0.05 | 0.3 | Yes | No | 60 | 20

## Unbalanced Faults
Test | Fault duration (s) | End Run (s) | Apply fault (s) | Fault type | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Tx_Tap | Xmin | Xmax | Action2 | Reduced DMAT
37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 9 | Yes | No |  | SCR | X/R
37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 12.6763 | 6.66 | 1 | 0 | No | [1.05,1.05] | 4 | 9 | Yes | Yes | POC - | [POC,10] | POC-14
37-3 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 2.2863 | 5.33 | 1 | 0 | No | [1.05,1.05] | 4 | 9 | Yes | Yes | High _scr
38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 9 | Yes | No | low_scr
39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 9 | Yes | No
41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | [1.05,1.05] | 4 | 9 | Yes | No
42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 12.6763 | 6.66 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | Yes
43-3 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 2.2863 | 5.33 | 0.05 | 0 | No | [1.05,1.05] | 4 | 9 | Yes | Yes
44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 9 | Yes | No
45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 9 | Yes | No
48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 9 | Yes | No
49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | No
49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 12.6763 | 6.66 | 1 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | Yes
49-3 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 2.2863 | 5.33 | 1 | 0 | No | [1.0375,1.0375] | 4 | 9 | Yes | Yes
50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | [1.05,1.05] | 4 | 12 | Yes | No
51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | [1.05,1.05] | 4 | 12 | Yes | No
52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 12 | Yes | No
53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 12 | Yes | No
54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | [1.05,1.05] | 4 | 11.1158 | Yes | No
55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 11.2602 | Yes | No
55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 12.6763 | 6.66 | 0.05 | 0 | No | [1.05,1.05] | 4 | 11.2602 | Yes | Yes
55-3 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 2.2863 | 5.33 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 11.4045 | Yes | Yes
56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 11.5489 | Yes | No
57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 11.6932 | Yes | No
58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 11.8376 | Yes | No
59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 11.982 | Yes | No
60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 12.1263 | Yes | No
61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 12.2707 | Yes | No
61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 12.6763 | 6.66 | 1 | 0 | No | [1.05,1.05] | 4 | 12.2707 | Yes | Yes
61-3 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 2.2863 | 5.33 | 1 | 0 | No | [1.05,1.05] | 4 | 12.415 | Yes | Yes
62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 12.5594 | Yes | No
63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 12.7038 | Yes | No
64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 12.8481 | Yes | No
65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | [1.05,1.05] | 4 | 12.9925 | Yes | No
66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 13.1368 | Yes | No
67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 13.2812 | Yes | No
67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 12.6763 | 6.66 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 13.2812 | Yes | Yes
67-3 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 2.2863 | 5.33 | 0.05 | 0 | No | [1.05,1.05] | 4 | 13.4256 | Yes | Yes
68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 13.5699 | Yes | No
69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 13.7143 | Yes | No
70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 13.8586 | Yes | No
71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 14.003 | Yes | No
72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 14.1474 | Yes | No
73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 14.2917 | Yes | No
73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 12.6763 | 6.66 | 1 | 0 | No | [1.0375,1.0375] | 4 | 14.2917 | Yes | Yes
73-3 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 2.2863 | 5.33 | 1 | 0 | No | [1.0375,1.0375] | 4 | 14.4361 | Yes | Yes
74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | [1.05,1.05] | 4 | 14.5805 | Yes | No
75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | [1.05,1.05] | 4 | 14.7248 | Yes | No
76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 14.8692 | Yes | No
77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 15.0135 | Yes | No
78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | [1.05,1.05] | 4 | 15.1579 | Yes | No
79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 15.3023 | Yes | No
79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 12.6763 | 6.66 | 0.05 | 0 | No | [1.05,1.05] | 4 | 15.3023 | Yes | Yes
79-3 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 2.2863 | 5.33 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 15.4466 | Yes | Yes
80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 15.591 | Yes | No
81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 15.7353 | Yes | No
82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 15.8797 | Yes | No
83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 16.0241 | Yes | No
84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 16.1684 | Yes | No
85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 16.3128 | Yes | No
85-2 | 2 | 12 | 5 | L-L | Zf=0 | 12.6763 | 6.66 | 1 | 0 | No | [1.05,1.05] | 4 | 16.3128 | Yes | Yes
85-3 | 2 | 12 | 5 | L-L | Zf=0 | 2.2863 | 5.33 | 1 | 0 | No | [1.05,1.05] | 4 | 16.4571 | Yes | Yes
86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 16.6015 | Yes | No
87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 16.7459 | Yes | No
88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 16.8902 | Yes | No
89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | [1.05,1.05] | 4 | 17.0346 | Yes | No
90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | [1.0375,1.0375] | 4 | 17.1789 | Yes | No
91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 17.3233 | Yes | No
91-2 | 2 | 12 | 5 | L-L | Zf=0 | 12.6763 | 6.66 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 17.3233 | Yes | Yes
91-3 | 2 | 12 | 5 | L-L | Zf=0 | 2.2863 | 5.33 | 0.05 | 0 | No | [1.05,1.05] | 4 | 17.4677 | Yes | Yes
92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 17.612 | Yes | No
93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 17.7564 | Yes | No
94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 17.9008 | Yes | No
95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | [1.05,1.05] | 4 | 18.0451 | Yes | No
96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 18.1895 | Yes | No
97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 18.3338 | Yes | No
97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 12.6763 | 6.66 | 1 | 0 | No | [1.0375,1.0375] | 4 | 18.3338 | Yes | No
97-3 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 2.2863 | 5.33 | 1 | 0 | No | [1.0375,1.0375] | 4 | 18.4782 | Yes | No
98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | [1.05,1.05] | 4 | 18.6226 | Yes | No
99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | [1.05,1.05] | 4 | 18.7669 | Yes | No
100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | [1.0375,1.0375] | 4 | 18.9113 | Yes | No
101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | [1.0375,1.0375] | 4 | 19.0556 | Yes | No
102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | [1.05,1.05] | 4 | 19.2 | Yes | No
103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 19.3444 | Yes | No
103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 12.6763 | 6.66 | 0.05 | 0 | No | [1.05,1.05] | 4 | 19.3444 | Yes | No
103-3 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 2.2863 | 5.33 | 0.05 | 0 | No | [1.0375,1.0375] | 4 | 19.4887 | Yes | No
104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 19.6331 | Yes | No
105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | [1.05,1.05] | 4 | 19.7774 | Yes | No
106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | [1.05,1.05] | 4 | 19.9218 | Yes | No
107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | [1.0375,1.0375] | 4 | 20.0662 | Yes | No
108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | [1.0375,1.0375] | 4 | 20.2105 | Yes | No
109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | [1.05,1.05] | 4 | 20.3549 | Yes | No
109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 12.6763 | 6.66 | 1 | 0 | No | [1.05,1.05] | 4 | 20.3549 | Yes | No
109_3 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 2.2863 | 5.33 | 1 | 0 | Yes | [1.05,1.05] | 4 | 20.4992 | Yes | No
110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | Yes | [1.0375,1.0375] | 4 | 20.6436 | Yes | No
111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | Yes | [1.0375,1.0375] | 4 | 20.788 | Yes | No
112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | Yes | [1.05,1.05] | 4 | 20.9323 | Yes | No
113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | Yes | [1.05,1.05] | 4 | 21.0767 | Yes | No
114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | Yes | [1.0375,1.0375] | 4 | 21.2211 | Yes | No
115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | Yes | [1.0375,1.0375] | 4 | 21.3654 | Yes | No
115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 12.6763 | 6.66 | 0.05 | 0 | Yes | [1.0375,1.0375] | 4 | 21.3654 | Yes | No
115-3 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 2.2863 | 5.33 | 0.05 | 0 | Yes | [1.05,1.05] | 4 | 21.5098 | Yes | No
116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | Yes | [1.05,1.05] | 4 | 21.6541 | Yes | No
117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | Yes | [1.0375,1.0375] | 4 | 21.7985 | Yes | No
118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | Yes | [1.0375,1.0375] | 4 | 21.9429 | Yes | No
119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | Yes | [1.05,1.05] | 4 | 22.0872 | Yes | No
120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | Yes | [1.05,1.05] | 4 | 22.2316 | Yes | No

## Temporary Over voltage
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Vgrid | Tx_Tap | Xmin | Xmax | Reduced DMAT
131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
137-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | Yes
137-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | Yes
138-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
138-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
139-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
139-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
146-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | Yes
146-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | Yes
147-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
147-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | -0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
148-1 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 12.6763 | 6.66 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No
148-2 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 2.2863 | 5.33 | 1 | 0.3 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8 | No

## MFRT
Test | End Run (s) | Apply Fault (s) | Fault duration (s) | Fault Impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Vgrid | Tx_Tap | Xmin | Xmax | Action | Reduced DMAT | Software
121 | 60 | 5 | S1 | 0.25 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 26 | No | Yes | PSCAD
121 | 60 | 5 | S1 | 0.25 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 26 | No | Yes | PSCAD
122 | 60 | 5 | S2 | S2 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | Yes | PSCAD
122 | 60 | 5 | S2 | S2 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | Yes | Yes | PSCAD
123 | 60 | 5 | S3 | S3 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSCAD
123 | 60 | 5 | S3 | S3 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSCAD
124 | 60 | 5 | S4 | S4 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSCAD
124 | 60 | 5 | S4 | S4 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSCAD
125 | 60 | 5 | S5 | S5 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | Yes | No | PSCAD
125 | 60 | 5 | S5 | S5 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSCAD
126 | 60 | 5 | P1 | P1 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 26 | No | Yes | PSSE
126 | 60 | 5 | P1 | P1 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 26 | No | Yes | PSSE
127 | 60 | 5 | P2 | P2 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | Yes | PSSE
127 | 60 | 5 | P2 | P2 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | Yes | PSSE
128 | 60 | 5 | P3 | P3 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE
128 | 60 | 5 | P3 | P3 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE
129 | 60 | 5 | P4 | row["Fault | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE
129 | 60 | 5 | P4 | P4 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE
130 | 60 | 5 | P5 | P5 | 12.6763 | 6.66 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE
130 | 60 | 5 | P5 | P5 | 2.2863 | 5.33 | 1 | 0 | 0.9983 | [1.05,1.05] | 4.8 | 47 | No | No | PSSE

## Voltage reference step
Test | End Run (s) | Apply step (s) | Event | Fig | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time | Reduced DMAT
149-1 | 25 | 5 | Vref | Fig2 | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
149-2 | 25 | 5 | Vref | Fig2 | 10 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
150-1 | 25 | 5 | Vref | Fig2 | 10 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
150-2 | 25 | 5 | Vref | Fig2 | 10 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
151-1 | 25 | 5 | Vref | Fig2 | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
151-2 | 25 | 5 | Vref | Fig2 | 3 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
152-1 | 25 | 5 | Vref | Fig2 | 3 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
152-2 | 25 | 5 | Vref | Fig2 | 3 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
153-1 | 25 | 5 | Vref | Fig2 | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
153-2 | 25 | 5 | Vref | Fig2 | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
154-1 | 25 | 5 | Vref | Fig2 | 12.6763 | 6.66 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
154-2 | 25 | 5 | Vref | Fig2 | 2.2863 | 5.33 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
155-1 | 25 | 5 | Vgrid | Fig3 | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
155-2 | 25 | 5 | Vgrid | Fig3 | 10 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
156-1 | 25 | 5 | Vgrid | Fig3 | 10 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
156-2 | 25 | 5 | Vgrid | Fig3 | 10 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
157-1 | 25 | 5 | Vgrid | Fig3 | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
157-2 | 25 | 5 | Vgrid | Fig3 | 3 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
158-1 | 25 | 5 | Vgrid | Fig3 | 3 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
158-2 | 25 | 5 | Vgrid | Fig3 | 3 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
159-1 | 25 | 5 | Vgrid | Fig3 | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
159-2 | 25 | 5 | Vgrid | Fig3 | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
160-1 | 25 | 5 | Vgrid | Fig3 | 12.6763 | 6.66 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
160-2 | 25 | 5 | Vgrid | Fig3 | 2.2863 | 5.33 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
161-1 | 25 | 5 | Qref | Fig4 | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
161-2 | 25 | 5 | Qref | Fig4 | 10 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
162-1 | 25 | 5 | Qref | Fig4 | 10 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
162-2 | 25 | 5 | Qref | Fig4 | 10 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
163-1 | 25 | 5 | Qref | Fig4 | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
163-2 | 25 | 5 | Qref | Fig4 | 3 | 3 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
164-1 | 25 | 5 | Qref | Fig4 | 3 | 14 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
164-2 | 25 | 5 | Qref | Fig4 | 3 | 3 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
165-1 | 25 | 5 | Qref | Fig4 | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
165-2 | 25 | 5 | Qref | Fig4 | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | Yes
166-1 | 25 | 5 | Qref | Fig4 | 12.6763 | 6.66 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No
166-2 | 25 | 5 | Qref | Fig4 | 2.2863 | 5.33 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20 | No

## Active Power reference
Test | End Run(s) | Apply step (s) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time | Reduced DMAT
167 | 35 | 5 | 10 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 28 | 5,15,25 | No
168 | 35 | 5 | 3 | 14 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 28 | 5,15,25 | No
169-1 | 35 | 5 | 12.6763 | 6.66 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 28 | 5,15,25 | Yes
169-2 | 35 | 5 | 2.2863 | 5.33 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 28 | 5,15,25 | Yes

## Grid Frequency
Test | End Run(s) | Apply step (s) | Test Profile | Freq ramp Hz/s | SCR | X/R | Available Power [%] | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time | Reduced DMAT | Time_steps (s) | Freq | Code
170-1 | 16 | 5 | 52-fast | 4 | 12.6763 | 6.66 | 1 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes | [0,5,25] | [50,52,50] | Profile
170-2 | 16 | 5 | 52-fast | 4 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-3 | 16 | 5 | 51p75-fast | 4 | 12.6763 | 6.66 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-4 | 16 | 5 | 51p75-fast | 4 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-5 | 16 | 5 | 51p5-fast | 4 | 12.6763 | 6.66 | 1 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-6 | 16 | 5 | 51p5-fast | 4 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-7 | 16 | 5 | 52-slow | 0.8 | 12.6763 | 6.66 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
170-8 | 16 | 5 | 52-slow | 0.8 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-1 | 16 | 5 | 52-fast | 4 | 12.6763 | 6.66 | 1 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-2 | 16 | 5 | 52-fast | 4 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-3 | 16 | 5 | 51p75-fast | 4 | 12.6763 | 6.66 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-4 | 16 | 5 | 51p75-fast | 4 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-5 | 16 | 5 | 51p5-fast | 4 | 12.6763 | 6.66 | 1 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-6 | 16 | 5 | 51p5-fast | 4 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-7 | 16 | 5 | 52-slow | 0.8 | 12.6763 | 6.66 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
171-8 | 16 | 5 | 52-slow | 0.8 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-1 | 16 | 5 | 52-fast | 4 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-2 | 16 | 5 | 52-fast | 4 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-3 | 16 | 5 | 51p75-fast | 4 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-4 | 16 | 5 | 51p75-fast | 4 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-5 | 16 | 5 | 51p5-fast | 4 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-6 | 16 | 5 | 51p5-fast | 4 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-7 | 16 | 5 | 52-slow | 0.8 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
172-8 | 16 | 5 | 52-slow | 0.8 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-1 | 16 | 5 | 52-fast | 4 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-2 | 16 | 5 | 52-fast | 4 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-3 | 16 | 5 | 51p75-fast | 4 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-4 | 16 | 5 | 51p75-fast | 4 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-5 | 16 | 5 | 51p5-fast | 4 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-6 | 16 | 5 | 51p5-fast | 4 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-7 | 16 | 5 | 52-slow | 0.8 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
173-8 | 16 | 5 | 52-slow | 0.8 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
174-1 | 16 | 5 | 47-fast | 4 | 12.6763 | 6.66 | 1 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
174-2 | 16 | 5 | 47-fast | 4 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
174-3 | 16 | 5 | 47-slow | 1.2 | 12.6763 | 6.66 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
174-4 | 16 | 5 | 47-slow | 1.2 | 2.2863 | 5.33 | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
175-1 | 16 | 5 | 47-fast | 4 | 12.6763 | 6.66 | 1 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
175-2 | 16 | 5 | 47-fast | 4 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
175-3 | 16 | 5 | 47-slow | 1.2 | 12.6763 | 6.66 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
175-4 | 16 | 5 | 47-slow | 1.2 | 2.2863 | 5.33 | 1 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
176-1 | 16 | 5 | 47-fast | 4 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
176-2 | 16 | 5 | 47-fast | 4 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
176-3 | 16 | 5 | 47-slow | 1.2 | 12.6763 | 6.66 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
176-4 | 16 | 5 | 47-slow | 1.2 | 2.2863 | 5.33 | 0.5 | 0.5 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
177-1 | 16 | 5 | 47-fast | 4 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
177-2 | 16 | 5 | 47-fast | 4 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
177-3 | 16 | 5 | 47-slow | 1.2 | 12.6763 | 6.66 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes
177-4 | 16 | 5 | 47-slow | 1.2 | 2.2863 | 5.33 | 0.05 | 0.05 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10 | Yes

## Grid voltage change – response
Test | End Run(s) | Apply event (s) | Test Profile | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Vgrid | Tx_Tap | Xmin | Xmax
178 | 15 | 5 | Fig8 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
179 | 15 | 5 | Fig8 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
180 | 15 | 5 | Fig8 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
181 | 15 | 5 | Fig8 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
182 | 15 | 5 | Fig9 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
183 | 15 | 5 | Fig9 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
184 | 15 | 5 | Fig9 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
185 | 15 | 5 | Fig9 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
182 | 15 | 5 | Fig10 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
183 | 15 | 5 | Fig10 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
184 | 15 | 5 | Fig10 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
185 | 15 | 5 | Fig10 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7

## Grid voltage phase angle change
Test | End Run(s) | Apply event (s) | Test Profile | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Vgrid | Tx_Tap | Xmin | Xmax
178 | 15 | 5 | Fig8 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
179 | 15 | 5 | Fig8 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
180 | 15 | 5 | Fig8 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
181 | 15 | 5 | Fig8 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
182 | 15 | 5 | Fig9 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
183 | 15 | 5 | Fig9 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
184 | 15 | 5 | Fig9 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
185 | 15 | 5 | Fig9 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
182 | 15 | 5 | Fig10 | [10] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
183 | 15 | 5 | Fig10 | [3] | [14,3] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
184 | 15 | 5 | Fig10 | [POC] | [POC] | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7
185 | 15 | 5 | Fig10 | [POC] | [POC] | 0.5 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7

## Grid Oscillation rejection test
Test | End Run(s) | Apply event (s) | Event | Magnitude | Step (Hz) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
190 | 20 | 5 | modulation frequency of 0.1Hz to 0.9Hz | 0.005 | 0.1 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 20 | 62
191 | 20 | 5 | modulation frequency of 1Hz to 45Hz | 0.005 | 1 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 20 | up tp 25
192 | 20 | 5 | In addition to amplitude modulation, at least 2 degree phase oscillation | 0.005 |  | POC | POC | 1 | 0 | No | 0.9983 | [1.05,1.05] |  |  | Optional

## Site specific FRT
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Retain voltage method | Tx_Tap | Xmin | Xmax
206 | 8 | 5 | 0.43 | Zf=0 | ~0 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
207 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
208 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
209 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
210 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
211 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
212 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
213 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
214 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
215 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 1 | 0 | Yes | 0.9983 | Imp | [1.05,1.05] | 4 | 8
216 | 8 | 5 | 0.43 | Zf=0 | 0 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
217 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
218 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
219 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
220 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
221 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
222 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
223 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
224 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
225 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 0.5 | 0 | Yes | 1.0174 | Imp | [1.05,1.05] | 4 | 8

## SCR1 active power test
Test | End Run(s) | Apply event (s) | Event | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
199-1 | 40 | 5 | Pref Step | 1 | 14 | 0.05 | 0 | Yes | 1.0575 | [1.0375,1.0375] | 4 | 40 | 5,15,20,25,35,40
199-2 | 40 | 5 | Pref Step | 1 | 3 | 0.05 | 0 | Yes | 1.0575 | [1.0375,1.0375] | 4 | 40 | 5,15,20,25,35,40

## SCR1 FRT
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
200-1 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 14 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6
200-2 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 3 | 1 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6
203-1 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 14 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6
203-2 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 3 | 1 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6

## Unbalance Fault(old)
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault type | Fault Impedance | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
37-1 | 9 | 5 | 0.43 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
37-2 | 9 | 5 | 0.43 | 2PHG | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
43-1 | 9 | 5 | 0.43 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
43-2 | 9 | 5 | 0.43 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
49-1 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
49-2 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
55-1 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
55-2 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
61-1 | 9 | 5 | 0.43 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
61-2 | 9 | 5 | 0.43 | 1PHG | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
67-1 | 9 | 5 | 0.43 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
67-2 | 9 | 5 | 0.43 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
73-1 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
73-2 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
79-1 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
79-2 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
85-1 | 12 | 5 | 2 | L-L | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 12
85-2 | 12 | 5 | 2 | L-L | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 12
91-1 | 12 | 5 | 2 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 12
91-2 | 12 | 5 | 2 | L-L | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 12