## System_inf
Var name | Var Val | unit
Workspacename
CaseName
POC Bus Name | 101
Terminal Bus Name | 102
V_POC | 1.034 | pu
Nominal Power | 150 | MW
Plant Capacity | 150 | MVA
Fault level | 901.186 | MVA
POC SCR | [12.676303,2.2863071]
POC XR ratio | [6.66,5.33]
POC base Voltage | 220 | kV
Nominal Frequency | 50 | Hz
Qlead,Qlag | [0.3,-0.3]
Save Format | csv | out,csv
Time step | 16.6667 | us
Channel plot | 200 | us
Q-V Droop | 0.05

## PPC_Signals
Signals | Variable | Value
PPC name
Pref
Qref | Qcm
PFref | PFref
Vdroop | Vref
id
iq
Inverter Name
Q_control_mode | Droop
Is Inside module activated? | No
Module Name

## V_droop
Qmax | Qmin | Qnom | P-slope | N-slope | deadband1 | deadband2 | deadband |  | Qbase-Vestas(MW) | Vref | Qoffset | Vmax
118.5 | -118.5 | 0 | 39.5 | 39.5 | 1 | 1 | 0 | 0.04 | 1.975 | 1 | 0 | 1.05

## Checklist
Checklist | Action
Flat Run | No
Snapshot | No
Balanced Fault | No
Unbalanced Fault | No
MFRT | No
Temporary Over Voltage | No
Voltage Reference Step Change | No
Active Power Reference Step | No
Grid Frequency | No
Grid Voltage Change | No
Grid Oscillation Rejection | No
Grid Voltage Phase Angle Change | No
SCR1 Active Power Ref Step | Yes
SCR1 FRT | No
Site specific SCR FRT | No

## Snapshot
Test | End Run (s) | Snapshot (s) | SCR | X/R | Active Power (pu) | Action | Reduced DMAT
0.4 | 5 | 3 | 10 | 6 | 1 | Yes | Yes
0.5 | 5 | 3 | 3 | 6 | 1 | Yes | No

## Flat Run
Test | End Run (s) | Store feed forward signals | SCR | X/R | Active Power (pu) | WTG Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
0.1 | 301 | enabled | POC,5 | POC,6 | 1 |  |  |  |  | Yes | Both | Reduced_DMAT
0.2 | 301 | disabled | POC,5 | POC,6 | 1 |  |  |  |  | Yes | PSCAD | Reduced_DMAT
0.3 | 301 | enabled | POC,5 | POC,6 | 0.05 |  |  |  |  | Yes | Both | Reduced_DMAT
0.4 | 5 | enabled | POC,10 | POC,6 | 1 |  |  |  |  | Yes | Both | Reduced_DMAT
0.5 | 5 | enabled | POC,3 | POC,6 | 1 |  |  |  |  | Yes | Both | DMAT
csr_s5251_1 | 20 | enabled | POC | POC |  | 1 | 0 | 0.9 | -1 | No | Both | CSR
csr_s5251_2 | 20 | enabled | POC | POC |  | 1 | 0 | 0.9 | 0 | No | Both | CSR
csr_s5251_3 | 20 | enabled | POC | POC |  | 1 | 0 | 0.9 | 1 | No | Both | CSR
csr_s5251_4 | 20 | enabled | POC | POC |  | 1 | 0 | 1.1 | -1 | No | Both | CSR
csr_s5251_5 | 20 | enabled | POC | POC |  | 1 | 0 | 1.1 | 0 | No | Both | CSR
csr_s5251_6 | 20 | enabled | POC | POC |  | 1 | 0 | 1.1 | 1 | No | Both | CSR
csr_s5251_7 | 20 | enabled | POC | POC |  | 1 | -1 | 0.9 | -1 | No | Both | CSR
csr_s5251_8 | 20 | enabled | POC | POC |  | 1 | -1 | 0.9 | 0 | No | Both | CSR
csr_s5251_9 | 20 | enabled | POC | POC |  | 1 | -1 | 0.9 | 1 | No | Both | CSR
csr_s5251_10 | 20 | enabled | POC | POC |  | 1 | -1 | 1.1 | -1 | No | Both | CSR
csr_s5251_11 | 20 | enabled | POC | POC |  | 1 | -1 | 1.1 | 0 | No | Both | CSR
csr_s5251_12 | 20 | enabled | POC | POC |  | 1 | -1 | 1.1 | 1 | No | Both | CSR
csr_s5251_13 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 0.9 | -1 | No | Both | CSR
csr_s5251_14 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 0.9 | 0 | No | Both | CSR
csr_s5251_15 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 0.9 | 1 | No | Both | CSR
csr_s5251_16 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 1.1 | -1 | No | Both | CSR
csr_s5251_17 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 1.1 | 0 | No | Both | CSR
csr_s5251_18 | 20 | enabled | POC | POC |  | 0.53333 | 1 | 1.1 | 1 | No | Both | CSR
csr_s5251_19 | 20 | enabled | POC | POC |  | 0 | 1 | 0.9 | -1 | No | Both | CSR
csr_s5251_20 | 20 | enabled | POC | POC |  | 0 | 1 | 0.9 | 0 | No | Both | CSR
csr_s5251_21 | 20 | enabled | POC | POC |  | 0 | 1 | 0.9 | 1 | No | Both | CSR
csr_s5251_22 | 20 | enabled | POC | POC |  | 0 | 1 | 1.1 | -1 | No | Both | CSR
csr_s5251_23 | 20 | enabled | POC | POC |  | 0 | 1 | 1.1 | 0 | No | Both | CSR
csr_s5251_24 | 20 | enabled | POC | POC |  | 0 | 1 | 1.1 | 1 | No | Both | CSR
csr_s5251_25 | 20 | enabled | POC | POC |  | 0 | -1 | 0.9 | -1 | No | Both | CSR
csr_s5251_26 | 20 | enabled | POC | POC |  | 0 | -1 | 0.9 | 0 | No | Both | CSR
csr_s5251_27 | 20 | enabled | POC | POC |  | 0 | -1 | 0.9 | 1 | No | Both | CSR
csr_s5251_28 | 20 | enabled | POC | POC |  | 0 | -1 | 1.1 | -1 | No | Both | CSR
csr_s5251_29 | 20 | enabled | POC | POC |  | 0 | -1 | 1.1 | 0 | No | Both | CSR
csr_s5251_30 | 20 | enabled | POC | POC |  | 0 | -1 | 1.1 | 1 | No | Both | CSR

## Balanced Fault
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault type | Fault impedance (pu) | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Software | Reduced DMAT
1 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
2 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | -0.3 | Yes | Both | DMAT
3 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 1 | 0.3 | Yes | Both | DMAT
4 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 1 | 0 | Yes | Both | DMAT
5 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | -0.3 | Yes | Both | DMAT
6 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 1 | 0.3 | Yes | Both | DMAT
7 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0 | Yes | Both | DMAT
8 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | -0.3 | Yes | Both | DMAT
9 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 10 | 14 | 0.05 | 0.3 | Yes | Both | DMAT
10 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 14 | 0.05 | 0 | Yes | Both | DMAT
11 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | -0.3 | Yes | Both | DMAT
12 | 10 | 5 | 0.43 | 3PHG | Zf=0 | ~0.0001 | 3 | 3 | 0.05 | 0.3 | Yes | Both | DMAT
13 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
14 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | -0.3 | Yes | Both | DMAT
15 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 1 | 0.3 | Yes | Both | DMAT
16 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 1 | 0 | Yes | Both | DMAT
17 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | -0.3 | Yes | Both | DMAT
18 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 1 | 0.3 | Yes | Both | DMAT
19 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0 | Yes | Both | DMAT
20 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | -0.3 | Yes | Both | DMAT
21 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 10 | 14 | 0.05 | 0.3 | Yes | Both | DMAT
22 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 14 | 0.05 | 0 | Yes | Both | DMAT
23 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | -0.3 | Yes | Both | DMAT
24 | 10 | 5 | 0.43 | 3PHG | Zf=Zs | ~0.5 | 3 | 3 | 0.05 | 0.3 | Yes | Both | DMAT
25 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0 | Yes | Both | DMAT
26 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | -0.3 | Yes | Both | DMAT
27 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 1 | 0.3 | Yes | Both | DMAT
28 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 1 | 0 | Yes | Both | DMAT
29 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | -0.3 | Yes | Both | DMAT
30 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 1 | 0.3 | Yes | Both | DMAT
31 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0 | Yes | Both | DMAT
32 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | -0.3 | Yes | Both | DMAT
33 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 10 | 14 | 0.05 | 0.3 | Yes | Both | DMAT
34 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 14 | 0.05 | 0 | Yes | Both | DMAT
35 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | -0.3 | Yes | Both | DMAT
36 | 10 | 5 | 0.5 | 3PHG | Zf=2xZs | ~0.7 | 3 | 3 | 0.05 | 0.3 | Yes | Both | DMAT

## Unbalanced Fault
Test | Fault duration (s) | End Run (s) | Apply fault (s) | Fault type | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT
37-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | No | No
37-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes
38 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | No
39 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | No
40 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 1 | 0 | No | No
41 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | No
42 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | No
43-1 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | No
43-2 | 0.43 | 9 | 5 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes
44 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | No
45 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | No
46 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | No
47 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | No
48 | 0.43 | 9 | 5 | 2PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | No
49-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | No
49-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes
50 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | No
51 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | No
52 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | No
53 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | No
54 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | No
55-1 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | No
55-2 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes
56 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | No
57 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | No
58 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | No
59 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | No
60 | 0.43 | 9 | 5 | 2PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | No
61-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | No | No
61-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 1 | 0 | No | Yes
62 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | -0.3 | No | No
63 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 1 | 0.3 | No | No
64 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 1 | 0 | No | No
65 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | -0.3 | No | No
66 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 1 | 0.3 | No | No
67-1 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | No | No
67-2 | 0.43 | 9 | 5 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | No | Yes
68 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | No
69 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | No
70 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 14 | 0.05 | 0 | No | No
71 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | No
72 | 0.43 | 9 | 5 | 1PHG | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | No
73-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | No | No
73-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | No | Yes
74 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | -0.3 | No | No
75 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0.3 | No | No
76 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 1 | 0 | No | No
77 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | -0.3 | No | No
78 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 1 | 0.3 | No | No
79-1 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | No | No
79-2 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | No | Yes
80 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | -0.3 | No | No
81 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0.3 | No | No
82 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 14 | 0.05 | 0 | No | No
83 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | -0.3 | No | No
84 | 0.43 | 9 | 5 | 1PHG | Zf=Zs | 3 | 3 | 0.05 | 0.3 | No | No
85-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0 | No | No
85-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 1 | 0 | No | Yes
86 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | -0.3 | No | No
87 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 1 | 0.3 | No | No
88 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 1 | 0 | No | No
89 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | -0.3 | No | No
90 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 1 | 0.3 | No | No
91-1 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | No | No
91-2 | 2 | 12 | 5 | L-L | Zf=0 | POC | POC | 0.05 | 0 | No | Yes
92 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | -0.3 | No | No
93 | 2 | 12 | 5 | L-L | Zf=0 | 10 | 14 | 0.05 | 0.3 | No | No
94 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 14 | 0.05 | 0 | No | No
95 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | -0.3 | No | No
96 | 2 | 12 | 5 | L-L | Zf=0 | 3 | 3 | 0.05 | 0.3 | No | No
97-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | No
97-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | No
98 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | No
99 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | No
100 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | No
101 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | No
102 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | No
103-1 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | No
103-2 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | No
104 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | No
105 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | No
106 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | No
107 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | No
108 | 0.43 | 9 | 5 | 2PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | No | No
109_1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0 | No | No
109_2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 1 | 0 | No | No
110 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | -0.3 | No | No
111 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 1 | 0.3 | No | No
112 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 1 | 0 | No | No
113 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | -0.3 | No | No
114 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 1 | 0.3 | No | No
115-1 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0 | No | No
115-2 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | POC | POC | 0.05 | 0 | No | No
116 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | -0.3 | No | No
117 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 10 | 14 | 0.05 | 0.3 | No | No
118 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 14 | 0.05 | 0 | No | No
119 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | -0.3 | No | No
120 | 0.43 | 9 | 5 | 1PHG | Zf=Rf = 1, 5 and 10 Ohm | 3 | 3 | 0.05 | 0.3 | Yes | No

## MFRT
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT | Software
121 | 60 | 5 | S1 | 0.25 | POC | POC | 1 | 0 | Yes | Yes | PSCAD
122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | Yes | Yes | PSCAD
123 | 60 | 5 | S3 | S3 | POC | POC | 1 | 0 | Yes | No | PSCAD
124 | 60 | 5 | S4 | S4 | POC | POC | 1 | 0 | Yes | No | PSCAD
125 | 60 | 5 | S5 | S5 | POC | POC | 1 | 0 | Yes | No | PSCAD
126 | 60 | 5 | P1 | P1 | POC | POC | 1 | 0 | No | Yes | PSSE
127 | 60 | 5 | P2 | P2 | POC | POC | 1 | 0 | No | Yes | PSSE
128 | 60 | 5 | P3 | P3 | POC | POC | 1 | 0 | No | No | PSSE
129 | 60 | 5 | P4 | P4 | POC | POC | 1 | 0 | No | No | PSSE
130 | 60 | 5 | P5 | P5 | POC | POC | 1 | 0 | No | No | PSSE

## Temporary Over Voltage
Test | End Run (s) | Apply fault (s) | Fault duration (s) | Fault impedance (pu) | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT
131 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | No
132 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | No
133 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | No
134 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | No
135 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | No
136 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | No
137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Yes
138 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | No
139 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | No
140 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0 | Yes | No
141 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | -0.3 | Yes | No
142 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 10 | 14 | 1 | 0.3 | Yes | No
143 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 14 | 1 | 0 | Yes | No
144 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | -0.3 | Yes | No
145 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | 3 | 3 | 1 | 0.3 | Yes | No
146 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | Yes
147 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | -0.3 | Yes | No
148 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0.3 | Yes | No

## Voltage Reference Step Change
Test | End Run (s) | Event | Time Steps (s) | Delta (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT
149 | 25 | Vref | fig2 | fig2 | 10 | 14,3 | 1 | 0 | Yes | No
150 | 25 | Vref | fig2 | fig2 | 10 | 14,3 | 0.05 | 0 | Yes | No
151 | 25 | Vref | fig2 | fig2 | 3 | 14,3 | 1 | 0 | Yes | No
152 | 25 | Vref | fig2 | fig2 | 3 | 14,3 | 0.05 | 0 | Yes | No
153 | 25 | Vref | fig2 | fig2 | POC | POC | 1 | 0 | Yes | Yes
154 | 25 | Vref | fig2 | fig2 | POC | POC | 0.05 | 0 | Yes | No
155 | 25 | Vgrid | fig3 | fig3 | 10 | 14,3 | 1 | 0 | Yes | No
156 | 25 | Vgrid | fig3 | fig3 | 10 | 14,3 | 0.05 | 0 | Yes | No
157 | 25 | Vgrid | fig3 | fig3 | 3 | 14,3 | 1 | 0 | Yes | No
158 | 25 | Vgrid | fig3 | fig3 | 3 | 14,3 | 0.05 | 0 | Yes | No
159 | 25 | Vgrid | fig3 | fig3 | POC | POC | 1 | 0 | Yes | Yes
160 | 25 | Vgrid | fig3 | fig3 | POC | POC | 0.05 | 0 | Yes | No
161 | 25 | Qref | fig4 | fig4 | 10 | 14,3 | 1 | 0 | Yes | No
162 | 25 | Qref | fig4 | fig4 | 10 | 14,3 | 0.05 | 0 | Yes | No
163 | 25 | Qref | fig4 | fig4 | 3 | 14,3 | 1 | 0 | Yes | No
164 | 25 | Qref | fig4 | fig4 | 3 | 14,3 | 0.05 | 0 | Yes | No
165 | 25 | Qref | fig4 | fig4 | POC | POC | 1 | 0 | Yes | Yes
166 | 25 | Qref | fig4 | fig4 | POC | POC | 0.05 | 0 | Yes | No

## Active Power Reference Step
Test | End Run (s) | SCR | X/R | Time Steps (s) | Pref_deltas (pu) | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT
167 | 35 | 10 | 14 | fig5 | fig5 | 1 | 0 | Yes | No
168 | 35 | 3 | 14 | fig5 | fig5 | 1 | 0 | Yes | No
169 | 35 | POC | POC | fig5 | fig5 | 1 | 0 | Yes | Yes

## Grid Frequency
Test | End Run (s) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | SCR | X/R | Available Power (%) | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
170 | 16 | fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
171 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
172 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
173 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
174 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
175 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
176 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
177 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
csr_s5253_1 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR | vre
csr_s5253_2 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_3 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_4 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_5 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_6 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_7 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_8 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_9 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_10 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_11 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_12 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_13 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_14 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_15 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_16 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_17 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_18 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_19 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_20 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_21 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_22 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_23 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_24 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_25 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_26 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_27 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_28 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_29 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_30 | 120 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_31 | 120 | [0,3,3.25,3.9167,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_32 | 120 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_33 | 600 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_34 | 1200 | [0,3,3.25,3.9167,1200] | [0,-1,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_35 | 1200 | [0,3,3.125,3.9167,120] | [0,-0.5,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_36 | 1200 | [0,3,3.125,3.9167,120] | [0,0.5,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_37 | 600 | [0,3,3.25,3.9167,120] | [0,1,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_38 | 120 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_39 | 600 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR

## Grid_F_extra
Test | End Run (s) | Time Steps (s) | Freq_Deltas (Hz) | Freq ramp Hz/s | SCR | X/R | Available Power (%) | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Action | Software | Suite
170 | 16 | fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
171 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
172 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
173 | 16 | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | [fig6_52-fast,fig6_51p75-fast,fig6_51p5-fast,fig6_52-slow] | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
174 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 1 | 1 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
175 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 1 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
176 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 0.5 | 0.5 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
177 | 16 | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | [fig7_47-fast,fig7_47-slow] | POC | POC | 0.05 | 0.05 | 0 |  |  |  |  | Yes | Both | Reduced_DMAT
csr_s5253_1 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_2 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_3 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_4 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_5 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_6 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_7 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_8 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_9 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_10 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_11 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_12 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_13 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_14 | 15 | [0,3,3.25,3.9167,15] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_15 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_16 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_17 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_18 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_19 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_20 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_21 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_22 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_23 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_24 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0.53333 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_25 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_26 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_27 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | 1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_28 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 0.984 | 1 | Yes | PSCAD | CSR
csr_s5253_29 | 15 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.034 | 0 | Yes | PSCAD | CSR
csr_s5253_30 | 120 | [0,3,3.25,3.5833,15] | [0,1,1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 0 | -1 | 1.084 | -1 | Yes | PSCAD | CSR
csr_s5253_31 | 120 | [0,3,3.25,3.9167,120] | [0,-1,-2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_32 | 120 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_33 | 600 | [0,3,3.25,3.5833,120] | [0,-1,-1,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_34 | 1200 | [0,3,3.25,3.9167,1200] | [0,-1,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_35 | 1200 | [0,3,3.125,3.9167,120] | [0,-0.5,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_36 | 1200 | [0,3,3.125,3.9167,120] | [0,0.5,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_37 | 600 | [0,3,3.25,3.9167,120] | [0,1,0,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_38 | 120 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR
csr_s5253_39 | 600 | [0,3,3.25,3.9167,120] | [0,1,2,0,0] | [false,true,true,false,false] | inf | inf |  |  |  | 1 | 0 | 1.034 | 0 | Yes | PSSE | CSR

## Grid Voltage Change
Test | End Run (s) | Time Steps (s) | Volt_delta (pu) | Ramp/Step | SCR | X/R | Active Power (pu) | Reactive Power (pu) | WTG_Pref (pu) | BESS_Pref (pu) | Vpoc (pu) | Qpoc (pu) | Software | Suite
178 | 65 | fig8 | fig8 | fig8 | 10 | 14,3 | 1 | 0 |  |  |  |  | Both | DMAT
179 | 65 | fig8 | fig8 | fig8 | 3 | 14,4 | 1 | 0 |  |  |  |  | Both | DMAT
180 | 65 | fig8 | fig8 | fig8 | POC | POC | 1 | 0 |  |  |  |  | Both | Reduced_DMAT
181 | 65 | fig8 | fig8 | fig8 | POC | POC | 0.5 | 0 |  |  |  |  | Both | Reduced_DMAT
182 | 45 | fig9 | fig9 | fig9 | 10 | 14,3 | 1 | 0 |  |  |  |  | Both | DMAT
183 | 65 | fig9 | fig9 | fig9 | 3 | 14,4 | 1 | 0 |  |  |  |  | Both | DMAT
184 | 65 | fig9 | fig9 | fig9 | POC | POC | 1 | 0 |  |  |  |  | Both | Reduced_DMAT
185 | 65 | fig9 | fig9 | fig9 | POC | POC | 0.5 | 0 |  |  |  |  | Both | Reduced_DMAT
186 | 65 | fig10_dip10,fig10_dip50,fig10_dip80 | fig10_dip10,fig10_dip50,fig10_dip80 | fig10_dip10,fig10_dip50,fig10_dip80 | 10 | 14,3 | 1 | 0 |  |  |  |  | Both | DMAT
187 | 65 | fig10_dip10,fig10_dip50,fig10_dip81 | fig10_dip10,fig10_dip50,fig10_dip81 | fig10_dip10,fig10_dip50,fig10_dip81 | 3 | 14,4 | 1 | 0 |  |  |  |  | Both | DMAT
188 | 65 | fig10_dip10,fig10_dip50,fig10_dip82 | fig10_dip10,fig10_dip50,fig10_dip82 | fig10_dip10,fig10_dip50,fig10_dip82 | POC | POC | 1 | 0 |  |  |  |  | Both | Reduced_DMAT
189 | 65 | fig10_dip10,fig10_dip50,fig10_dip83 | fig10_dip10,fig10_dip50,fig10_dip83 | fig10_dip10,fig10_dip50,fig10_dip83 | POC | POC | 0.5 | 0 |  |  |  |  | Both | Reduced_DMAT
csr_s5254_1 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_2 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_3 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_4 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_5 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_6 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_7 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_8 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 2 | 1.034 | 0 | PSCAD | CSR
csr_s5254_9 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 3 | 1.084 | -1 | PSCAD | CSR
csr_s5254_10 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_11 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_12 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_13 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_14 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_15 | 10 | [0,5,5.2,10] | [0,0.3,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_16 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_17 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_18 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_19 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_20 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_21 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_22 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_23 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 2 | 1.034 | 0 | PSCAD | CSR
csr_s5254_24 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 3 | 1.084 | -1 | PSCAD | CSR
csr_s5254_25 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_26 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_27 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_28 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_29 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_30 | 15 | [0,5,7,10] | [0,0.25,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_31 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_32 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_33 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_34 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_35 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_36 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_37 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_38 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 2 | 1.034 | 0 | PSCAD | CSR
csr_s5254_39 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 3 | 1.084 | -1 | PSCAD | CSR
csr_s5254_40 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_41 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_42 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_43 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_44 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_45 | 10 | [0,5,25,10] | [0,0.2,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_46 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_47 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_48 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_49 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_50 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_51 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_52 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_53 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 2 | 1.034 | 0 | PSCAD | CSR
csr_s5254_54 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 3 | 1.084 | -1 | PSCAD | CSR
csr_s5254_55 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_56 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_57 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_58 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_59 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_60 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_61 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 0.984 | 1 | PSCAD | CSR
csr_s5254_62 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.034 | 0 | PSCAD | CSR
csr_s5254_63 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | 0 | 1.084 | -1 | PSCAD | CSR
csr_s5254_64 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_65 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_66 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 1 | -1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_67 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_68 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 2 | 1.034 | 0 | PSCAD | CSR
csr_s5254_69 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0.53333 | 3 | 1.084 | -1 | PSCAD | CSR
csr_s5254_70 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_71 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_72 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | 1 | 1.084 | -1 | PSCAD | CSR
csr_s5254_73 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 0.984 | 1 | PSCAD | CSR
csr_s5254_74 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.034 | 0 | PSCAD | CSR
csr_s5254_75 | 60 | [0,5,40,10] | [0,0.15,0,0] | [false,false,false,false] | inf | inf |  |  | 0 | -1 | 1.084 | -1 | PSCAD | CSR

## Grid Oscillation Rejection
Test | End Run (s) | Time Steps (s) | Osc_freq | Magnitude | Step (Hz) | SCR | X/R | Osc_Phase_deg | Active Power (pu) | Reactive Power | Action | Reduced DMAT
190 | 20 | [5,15] | 0.1:0.9 | 0.005 | 0.1 | POC | POC | 0 | 1 | 0 | Yes | Yes
191 | 20 | [5,15] | 1:45 | 0.005 | 1 | POC | POC | 0 | 1 | 0 | No | Yes
192 | 20 | [5,15] | 0.1:0.9,1:45 | 0.005 | 0.1,1 | POC | POC | 2 | 1 | 0 | No | No

## Grid Voltage Phase Angle Change
Test | End Run (s) | Apply event (s) | Angle Change | SCR | X/R | Active Power (pu) | Reactive Power (pu) | Action | Reduced DMAT
193 | 35 | 5 | 40,-40,60,-60 | 10 | 14,3 | 1 | 0 | Yes | No
194 | 35 | 5 | 40,-40,60,-61 | 10 | 14,4 | 0.05 | 0 | No | No
195 | 35 | 5 | 40,-40,60,-62 | 3 | 14,5 | 1 | 0 | No | No
196 | 35 | 5 | 40,-40,60,-63 | 3 | 14,6 | 0.05 | 0 | No | No
197 | 35 | 5 | 40,-40,60,-64 | POC | POC | 1 | 0 | No | Yes
198 | 35 | 5 | 40,-40,60,-65 | POC | POC | 0.05 | 0 | No | No

## SCR1 Active Power Ref Step
Test | Time Steps (s) | Pref_deltas (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Reduced DMAT | End Run (s)
199 | fig12 | fig12 | 1 | 14,3 | 0.05 | 0 | Yes | Yes | 35

## SCR1 FRT
Test | End Run (s) | Apply Fault (s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR_preF | SCR_postF | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Reduced DMAT
200 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 1 | [14,3] | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6 | Yes
201 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 1 | [14,3] | 0.5 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6 | No
202 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 1 | [14,3] | 0.05 | 0 | Yes | 2.0058 | [1.05,1.05] | 4 | 6 | No
203 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 1 | [14,3] | 1 | 0 | Yes | 3.0058 | [1.05,1.05] | 4 | 6 | Yes
204 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 1 | [14,3] | 0.5 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6 | No
205 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 1 | [14,3] | 0.05 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6 | No

## Site specific SCR FRT
Test | End Run (s) | Apply Fault (s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Retain voltage method | Tx_Tap | Xmin | Xmax | Reduced DMAT
206 | 8 | 5 | 0.43 | Zf=0 | ~0 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
207 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
208 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
209 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
210 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
211 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
212 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
213 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
214 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
215 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 1 | 0 | Yes | 0.9983 | Imp | [1.05,1.05] | 4 | 8 | Yes
216 | 8 | 5 | 0.43 | Zf=0 | 0 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
217 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
218 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
219 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
220 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
221 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
222 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
223 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
224 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes
225 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 0.5 | 0 | Yes | 1.0174 | Imp | [1.05,1.05] | 4 | 8 | Yes

## Figure References
Suite | Type | Figure | Time_steps | Deltas | Ramp
DMAT | Vref Step | fig2 | [0,5,15,25,35,45] | [0,0.05,-0.05,-0.05,0.05,0] | [false,false,false,false,false,false]
DMAT | Grid Voltage Step | fig3 | [0,5,15,25,35,45] | [0,0.05,-0.05,-0.05,0.05,0] | [false,false,false,false,false,false]
DMAT | Qref Step | fig4 | [0,5,15,25,35,45] | [0,-0.3,0.6,-0.6,0.3,0] | [false,false,false,false,false,false]
DMAT | Pref Step | fig5 | [0,5,15,25,35] | [0,-0.5,-0.45,0.95,0] | [false,false,false,false,false]
DMAT | Freq Step | fig6_52-fast | [0,5,15,25] | [0,2,-2,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p75-fast | [0,5,15,25] | [0,1.75,-1.75,0] | [false,false,false,false]
DMAT | Freq Step | fig6_51p5-fast | [0,5,15,25] | [0,1.5,-1.5,0] | [false,false,false,false]
DMAT | Freq Step | fig6_52-slow | [0,5,8,15,18,25] | [0,2,0,-2,0,0] | [false,true,false,true,false,false]
DMAT | Freq Step | fig7_47-fast | [0,5,15,25] | [0,-3,3,0] | [false,false,false,false]
DMAT | Freq Step | fig7_47-slow | [0,5,8,15,18,25] | [0,-3,0,3,0,0] | [false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig8 | [0,5,11,20,26,35,41,50,56,65] | [0,-0.1,0,0.2,0,-0.2,0,0.1,0,0] | [false,true,false,true,false,true,false,true,false,false]
DMAT | Grid Voltage Step | fig9 | [0,5,15,25,35,45] | [0,0.1,-0.2,0.2,-0.1,0] | [false,false,false,false,false]
DMAT | Grid Voltage Step | fig10_dip10 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.9,0.7,0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.5,0.3,0.2,0,0] | [false,false,false,true,false,false]
DMAT | Grid Voltage Step | fig10_dip50 | [0,5,5.499,5.5001,6.5001,12] | [0,-0.5,0.3,0.2,0,0] | [false,false,false,true,false,false]
DMAT | Pref Step SCR 1 | fig12 | [0,5,10,15,20,25,30,35] | [0.15,0.2,0.4,0.6,0.8,1,1] | [false,false,false,false,false,false,false,false]