## System_inf
Var name | Var Val | unit
Workspacename
CaseName
POC Bus Name | 101
Terminal Bus Name | 102
V_POC | 1.034 | pu
Nominal Power | 150 | MW
Plant Capacity | 150 | MVA
Fault level | 901.186 | MVA
POC SCR | [1.3 7]
POC XR ratio | 2.7744
POC base Voltage | 220 | kV
Nominal Frequency | 50 | Hz
Qlead,Qlag | [0.3,-0.3]
Save Format | csv | out,csv
Time step | 16.6667 | us
Channel plot | 200 | us

## PPC_Signals
Signals | Variable | Value
PPC name
Pref
Qref | Qcm
PFref | PFref
Vdroop | Vref
id
iq
Inverter Name
Q_control_mode | Droop
Is Inside module activated? | No
Module Name

## V_droop
Qmax | Qmin | Qnom | P-slope | N-slope | deadband1 | deadband2 | deadband |  | Qbase-Vestas(MW) | Vref | Qoffset | Vmax
118.5 | -118.5 | 0 | 39.5 | 39.5 | 1 | 1 | 0 | 0.04 | 1.975 | 1 | 0 | 1.05

## Checklist
Checklist | Action
Flat Run | Yes
Snapshot | No
Balance Fault | No
Unbalance Fault | No
MFRT | No
Temporary Over voltage | No
Voltage reference step change | No
Active Power reference | No
Grid Frequency | Yes
Grid voltage change – response | No
Grid Oscillation rejection test | No
Grid voltage phase angle change | No
SCR1 active power test | No
SCR1 FRT | No
Site specific FRT | Yes

## Flat Run
Test | End Run | Store feed forward signals | SCR | X/R | Active Power (pu) | Action | Vgrid | Tx_Tap | Xmin | Xmax
1 | 301 | enabled | 5 | 6 | 1 | No | 1.0456 | [1.05,1.05] | 1 | 301
2 | 301 | disabled | 5 | 6 | 1 | No | 1.0456 | [1.05,1.05] | 1 | 301
3 | 301 | enabled | 5 | 6 | 0.05 | Yes | 1.0569 | [1.05,1.0375] | 1 | 301
4 | 5 | enabled | 5 | 6 | 1 | No | 1.0456 | [1.05,1.05] | 3 | 5
5 | 5 | enabled | 3 | 2.7 | 2 | No | 0.9983 | [1.05,1.05] | 3 | 5

## Snapshot
Test | End Run (s) | snapshot (s) | SCR | X/R | Active Power (pu) | Action
4 | 5 | 3 | 10 | 6 | 1 | Yes
5 | 5 | 3 | 3 | 6 | 1 | Yes

## Unbalance Fault
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault type | Fault Impedance | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
37-1 | 9 | 5 | 0.43 | 2PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
37-2 | 9 | 5 | 0.43 | 2PHG | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
43-1 | 9 | 5 | 0.43 | 2PHG | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
43-2 | 9 | 5 | 0.43 | 2PHG | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
49-1 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
49-2 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
55-1 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
55-2 | 9 | 5 | 0.43 | 2PHG | Zf=Zs | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
61-1 | 9 | 5 | 0.43 | 1PHG | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
61-2 | 9 | 5 | 0.43 | 1PHG | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
67-1 | 9 | 5 | 0.43 | 1PHG | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
67-2 | 9 | 5 | 0.43 | 1PHG | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
73-1 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 9
73-2 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 9
79-1 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 9
79-2 | 9 | 5 | 0.43 | 1PHG | Zf=Zs | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 9
85-1 | 12 | 5 | 2 | L-L | Zf=0 | 10 | 14 | 1 | 0 | Yes | 1.0573 | [1.05,1.05] | 4 | 12
85-2 | 12 | 5 | 2 | L-L | Zf=0 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 12
91-1 | 12 | 5 | 2 | L-L | Zf=0 | 10 | 14 | 0.05 | 0 | Yes | 1.0595 | [1.0375,1.0375] | 4 | 12
91-2 | 12 | 5 | 2 | L-L | Zf=0 | POC | POC | 0.05 | 0 | Yes | 1.0546 | [1.0375,1.0375] | 4 | 12

## MFRT
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
121 | 60 | 5 | S1 | S1 | POC | POC | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4.8 | 26
122 | 60 | 5 | S2 | S2 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.8 | 47

## Temporary Over voltage
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
137 | 8 | 5 | 0.9 | Yf = jXc (U_Ov = 1.15pu) | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8
146 | 8 | 5 | 0.1 | Yf = jXc (U_Ov = 1.2pu) | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 8

## Voltage reference step
Test | End Run(s) | Apply step (s) | Event | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
153 | 25 | 5 | Vref | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20
159 | 25 | 5 | Vgrid_step | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20
165-1 | 25 | 5 | Qref | POC | POC | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20
165-2 | 25 | 5 | PFref | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5,10,15,20

## Active Power reference
Test | End Run(s) | Apply step (s) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
169 | 28 | 5 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 28 | 5,13,18

## Grid Frequency
Test | End Run(s) | Apply step (s) | Freq target | Freq ramp Hz/s | SCR | X/R | Available Power [%] | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
170-1 | 16 | 5 | 52 | 4 | POC | POC | 1 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10
170-2 | 16 | 5 | 51.75 | 4 | POC | POC | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10
170-3 | 16 | 5 | 51.5 | 4 | POC | POC | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10
170-4 | 16 | 5 | 52 | 0.66667 | POC | POC | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 16 | 5,10
171-1 | 16 | 5 | 52 | 4 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 16 | 5,10
171-2 | 16 | 5 | 51.75 | 4 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 16 | 5,10
171-3 | 16 | 5 | 51.5 | 4 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 16 | 5,10
171-4 | 16 | 5 | 52 | 0.66667 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 16 | 5,10
172-1 | 18 | 5 | 52 | 4 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
172-2 | 18 | 5 | 51.75 | 4 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
172-3 | 18 | 5 | 51.5 | 4 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
172-4 | 18 | 5 | 52 | 0.66667 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
173-1 | 18 | 5 | 52 | 4 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
173-2 | 18 | 5 | 51.75 | 4 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
173-3 | 18 | 5 | 51.5 | 4 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
173-4 | 18 | 5 | 52 | 0.66667 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
174-1 | 18 | 5 | 47.001 | 4 | POC | POC | 1 | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 18 | 5,10
174-2 | 18 | 5 | 47 | 0.66667 | POC | POC | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 18 | 5,10
175-1 | 18 | 5 | 47 | 4 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
175-2 | 18 | 5 | 47 | 0.66667 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
176-1 | 18 | 5 | 47 | 4 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
176-2 | 18 | 5 | 47 | 0.66667 | POC | POC | 0.5 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 18 | 5,10
177-1 | 18 | 5 | 47 | 4 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
177-2 | 18 | 5 | 47 | 0.66667 | POC | POC | 0.05 | 0.05 | 0 | No | 1.0546 | [1.0375,1.0375] | 4 | 18 | 5,10
226 | 18 | 5 | 47 | 0.66667 | POC | POC | 1 | 1 | 0 | No | 0.9983 | [1.05,1.05] | 4 | 6 | 5,10
228 | 18 | 5 | 47 | 0.66667 | POC | POC | 1 | 0.5 | 0 | No | 1.0174 | [1.05,1.05] | 4 | 6 | 5,10

## Grid voltage phase angle change
Test | End Run(s) | Apply event (s) | Event | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
197 | 8 | 5 | Angle step ±40° and ±60° | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4.9 | 7 | only +-40

## Grid voltage change – response
Test | End Run(s) | Apply step (s) | Event | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
180 | 50 | 5 | voltage ramp | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 50 | 5,15,30,40
181 | 50 | 5 | voltage ramp | POC | POC | 0.5 | 0 | Yes | 1.0174 | [1.05,1.05] | 4 | 50 | 5,15,30,40
184 | 50 | 5 | 10% voltage step | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 50 | 5,15,30,40
185 | 50 | 5 | 10% voltage step | POC | POC | 0.5 | 0 | Yes | 1.0174 | [1.05,1.05] | 4 | 50 | 5,15,30,40
188-1 | 25 | 5 | Extended dip voltage=0.8 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5
188-2 | 25 | 5 | Extended dip voltage=0.5 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5
188-3 | 25 | 5 | Extended dip voltage=0.1 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 25 | 5
189-1 | 25 | 5 | Extended dip voltage=0.8 | POC | POC | 0.5 | 0 | Yes | 1.0174 | [1.05,1.05] | 4 | 25 | 5
189-2 | 25 | 5 | Extended dip voltage=0.5 | POC | POC | 0.5 | 0 | Yes | 1.0174 | [1.05,1.05] | 4 | 25 | 5
189-3 | 25 | 5 | Extended dip voltage=0.1 | POC | POC | 0.5 | 0 | Yes | 1.0174 | [1.05,1.05] | 4 | 25 | 5

## Grid Oscillation rejection test
Test | End Run(s) | Apply event (s) | Event | Magnitude | Step (Hz) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
190 | 20 | 5 | modulation frequency of 0.1Hz to 0.9Hz | 0.005 | 0.1 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 20 | 62
191 | 20 | 5 | modulation frequency of 1Hz to 45Hz | 0.005 | 1 | POC | POC | 1 | 0 | Yes | 0.9983 | [1.05,1.05] | 4 | 20 | up tp 25
192 | 20 | 5 | In addition to amplitude modulation, at least 2 degree phase oscillation | 0.005 |  | POC | POC | 1 | 0 | No | 0.9983 | [1.05,1.05] |  |  | Optional

## Site specific FRT
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Retain voltage method | Tx_Tap | Xmin | Xmax
206 | 8 | 5 | 0.43 | Zf=0 | ~0 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
207 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
208 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
209 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
210 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
211 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
212 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
213 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
214 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 1 | 0 | No | 0.9983 | Imp | [1.05,1.05] | 4 | 8
215 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 1 | 0 | Yes | 0.9983 | Imp | [1.05,1.05] | 4 | 8
216 | 8 | 5 | 0.43 | Zf=0 | 0 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
217 | 8 | 5 | 0.43 | Zf=0.11 x Zs | ~0.1 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
218 | 8 | 5 | 0.43 | Zf=0.25 x Zs | ~0.2 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
219 | 8 | 5 | 0.43 | Zf=0.42 x Zs | ~0.3 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
220 | 8 | 5 | 0.43 | Zf=0.66 x Zs | ~0.4 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
221 | 8 | 5 | 0.43 | Zf=1x Zs | ~0.5 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
222 | 8 | 5 | 0.43 | Zf=1.5 x Zs | ~0.6 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
223 | 8 | 5 | 0.43 | Zf=2.3 x Zs | ~0.7 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
224 | 8 | 5 | 0.43 | Zf=4 x Zs | ~0.8 | POC | POC | 0.5 | 0 | No | 1.0174 | Imp | [1.05,1.05] | 4 | 8
225 | 8 | 5 | 0.43 | Zf=9 x Zs | ~0.9 | POC | POC | 0.5 | 0 | Yes | 1.0174 | Imp | [1.05,1.05] | 4 | 8

## SCR1 active power test
Test | End Run(s) | Apply event (s) | Event | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax | Steps Time
199-1 | 40 | 5 | Pref Step | 1 | 14 | 0.05 | 0 | Yes | 1.0575 | [1.0375,1.0375] | 4 | 40 | 5,15,20,25,35,40
199-2 | 40 | 5 | Pref Step | 1 | 3 | 0.05 | 0 | Yes | 1.0575 | [1.0375,1.0375] | 4 | 40 | 5,15,20,25,35,40

## SCR1 FRT
Test | End Run(s) | Apply Fault(s) | Fault duration(s) | Fault Impedance | Applied Fault Voltage (pu) | SCR | X/R | Active Power (pu) | Reactive Power | Action | Vgrid | Tx_Tap | Xmin | Xmax
200-1 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 14 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6
200-2 | 8 | 5 | 0.43 | Zf=4xZs | ~ 0.8pu | 3 | 3 | 1 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6
203-1 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 14 | 1 | 0 | Yes | 1.0839 | [1.05,1.05] | 4 | 6
203-2 | 8 | 5 | 0.43 | Zf=0 | 0 | 3 | 3 | 1 | 0 | Yes | 1.0058 | [1.05,1.05] | 4 | 6